## Blend Ratio
Plant Baseline | Rate |  | % composition | Normalized to 1000 mL | x7 | normalize 700 ml
WLS Streams |  | outlet | 947
De-oiled Water | 820 |  | 86.5892 | 865.8923 | 6061.246 | 606.1246
HLS Sludge | 75 |  | 7.9197 | 79.1975 | 554.3823 | 55.4382
Low Pressure BD | 0 |  | 0 | 0 | 0 | 0
Make up Water | 20 |  | 2.1119 | 21.1193 | 147.8353 | 14.7835
Lime | 16 |  | 1.6895 | 16.8955 | 118.2682 | 11.8268
Mag | 16 |  | 1.6895 | 16.8955 | 118.2682 | 11.8268
| 947 |  | 100 | 1000 | 7000 | 700
| 1% | 0.1%
ppm | 10000 | 1000
1 mL in 1L | 10 | 1
1 mL in .7 L | 14.2857 | 1.4286
required dosage (ppm) | 80 | 8
# mL in 1L | 8 | 8
# mL in 0.7 L | 5.6 | 5.6
required dosage (ppm) | # mL in 1L | # mL in 0.7 L |  | required dosage (ppm) | # mL in 1L | # mL in 0.7 L
10 | 1 | 0.69979 |  | 1 | 1 | 0.69979
20 | 2 | 1.3996 |  | 2 | 2 | 1.3996
30 | 3 | 2.0994 |  | 3 | 3 | 2.0994
40 | 4 | 2.7992 |  | 4 | 4 | 2.7992
50 | 5 | 3.499 |  | 5 | 5 | 3.499
60 | 6 | 4.1987 |  | 6 | 6 | 4.1987
70 | 7 | 4.8985 |  | 7 | 7 | 4.8985
80 | 8 | 5.5983 |  | 8 | 8 | 5.5983
90 | 9 | 6.2981 |  | 9 | 9 | 6.2981
100 | 10 | 6.9979 |  | 10 | 10 | 6.9979
110 | 11 | 7.6977 |  | 11 | 11 | 7.6977
120 | 12 | 8.3975 |  | 12 | 12 | 8.3975
130 | 13 | 9.0973
140 | 14 | 9.7971
150 | 15 | 10.4969

## Procedure
Composite Procedure: prepare composite sample with produced water, sludge, MgO & lime all mixed together. Fill jars and add coag while stirring at 200 rpm for 60s, add floc & let stir for 30s, reduce to 100 rpm for 2 mins, then let settle for 5 mins before collecting samples.
Composite minus sludge Procedure:
Slurry Procedure:
NOTE:
2490 is CLAR 2537A
1580 is CLAR17650

## Jan 2022
PHASE F JAR TESTING
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
1/20/22 | standard | 1 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 999 | 6 | 999 | 99.3 | 899.7 | 7767 settled faster with all coags but 7878 did give a better water quality
|  |  | 2 | 7767 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7767 | 613 | 4
|  |  | 3 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 195 | 2
|  |  | 4 | 7767 | 0.5 | 1580 | 10 | 10 ppm:1580 0.5 ppm:7767 | 700 | 5
|  |  | 5 | 7878 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7878 | 344 | 3
|  |  | 6 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 99.3 | 1
1/20/22 | standard | 2 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 915 | 6 | 915 | 249 | 666 | visually theres little difference, may settle faster with more coag but not significantly
|  |  | 2 | 7767 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:7767 | 662 | 5
|  |  | 3 | 7767 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7767 | 487 | 4
|  |  | 4 | 7767 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:7767 | 375 | 3
|  |  | 5 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 273 | 2
|  |  | 6 | 7767 | 0.5 | 2537A | 25 | 25 ppm:2537A 0.5 ppm:7767 | 249 | 1
1/20/22 |  | 3 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 999 | 6 | 999 | 245 | 754 | big difference with increasing floc, particle size is much bigger with a good gradient and there is increasingly more FW during the stir period. Settling is also increase with more floc. Water clarity still isn't amazing, jars are very hazy.
|  |  | 2 | 7767 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:7767 | 691 | 5
|  |  | 3 | 7767 | 1 | 2537A | 5 | 5 ppm:2537A 1 ppm:7767 | 451 | 4
|  |  | 4 | 7767 | 1.5 | 2537A | 5 | 5 ppm:2537A 1.5 ppm:7767 | 310 | 3
|  |  | 5 | 7767 | 2 | 2537A | 5 | 5 ppm:2537A 2 ppm:7767 | 303 | 2
|  |  | 6 | 7767 | 2.5 | 2537A | 5 | 5 ppm:2537A 2.5 ppm:7767 | 245 | 1
1/20/22 |  | 4 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 999 | 6 | 999 | 96.7 | 902.3
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 430 | 5
|  |  | 3 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 242 | 4
|  |  | 4 | 7767 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:7767 | 146 | 3
|  |  | 5 | 7767 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:7767 | 130 | 2
|  |  | 6 | 7767 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:7767 | 96.7 | 1
1/20/22 |  | 5 | 1 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 170 | 2 | 464 | 122 | 342 | 7767 is clearly showing the best particle formation. 7878 shows the worst particle size and settling rate.
|  |  | 2 | 7878 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7878 | 280 | 3
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 122 | 1
|  |  | 4 | 7767 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 | 356 | 4
|  |  | 5 | 7878 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7878 | 464 | 6
|  |  | 6 | 8181 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:8181 | 386 | 5
1/20/22 |  | 6 | 1 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 119 | 5 | 208 | 28.4 | 179.6 | some difference between the coags but all seemed to have very similar performance with particle size & settling
|  |  | 2 | 7767 | 1 | 2490 | 20 | 20 ppm:2490 1 ppm:7767 | 37.7 | 2
|  |  | 3 | 7767 | 1 | 2495 | 20 | 20 ppm:2495 1 ppm:7767 | 28.4 | 1
|  |  | 4 | 7767 | 1 | 8190 | 20 | 20 ppm:8190 1 ppm:7767 | 208 | 6
|  |  | 5 | 7767 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 | 113 | 4
|  |  | 6 | 7767 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:7767 | 110 | 3
| use phase F sludge | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 42.6 | 956.4 | 7767 still had the best particle size then followed by 8182. J4 visible FW during stir & settled fastest. J4 still looked the best in all aspects
|  |  | 2 | 2531 | 1 | 1252 | 20 | 20 ppm:1252 1 ppm:2531 | 119 | 4
|  |  | 3 | 2531 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:2531 | 42.6 | 1
|  |  | 4 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 52.3 | 2
|  |  | 5 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 59 | 3
|  |  | 6 | 8182 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8182 | 292 | 5
| use phase G sludge | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 400 | 6 | 400 | 5.81 | 394.19 | similar sludge as F. Settling rate J4>J2>J3>J5>J6…very good water quality, sampled after 1 min settling. J4 showed best size and settling rate, lots of FW.
|  |  | 2 | 2531 | 1 | 1252 | 20 | 20 ppm:1252 1 ppm:2531 | 20.1 | 3
|  |  | 3 | 2531 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:2531 | 12.4 | 2
|  |  | 4 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 5.81 | 1
|  |  | 5 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 35.2 | 4
|  |  | 6 | 8182 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8182 | 43.1 | 5
| back to F phase sludge | 9 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 7.33 | 991.67 | there was an increase in size just with coag addition and with floc there was still a good gradient. Even during the slow mix there was an increase in FW with the coag increase. Measured turb at 2 min
|  |  | 2 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 59 | 5
|  |  | 3 | 7767 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7767 | 48 | 4
|  |  | 4 | 7767 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:7767 | 30.6 | 3
|  |  | 5 | 7767 | 1 | 2537A | 40 | 40 ppm:2537A 1 ppm:7767 | 13.6 | 2
|  |  | 6 | 7767 | 1 | 2537A | 50 | 50 ppm:2537A 1 ppm:7767 | 7.33 | 1