## Blend Ratio
Plant Baseline | Rate |  | % composition | Normalized to 1000 mL | x7 | normalize 700 ml
WLS Streams |  | outlet | 967
De-oiled Water | 840 |  | 86.8666 | 868.666 | 6080.6618 | 608.0662
HLS Sludge | 85 |  | 8.7901 | 87.9007 | 615.3051 | 61.5305
Low Pressure BD | 0 |  | 0 | 0 | 0 | 0
Make up Water | 10 |  | 1.0341 | 10.3413 | 72.3888 | 7.2389
Lime | 16 |  | 1.6546 | 16.546 | 115.8221 | 11.5822
Mag | 16 |  | 1.6546 | 16.546 | 115.8221 | 11.5822
| 967 |  | 100 | 1000 | 7000 | 700
| 1% | 0.1%
ppm | 10000 | 1000
1 mL in 1L | 10 | 1
1 mL in .7 L | 14.2857 | 1.4286
required dosage (ppm) | 80 | 8
# mL in 1L | 8 | 8
# mL in 0.7 L | 5.6 | 5.6
required dosage (ppm) | # mL in 1L | # mL in 0.7 L |  | required dosage (ppm) | # mL in 1L | # mL in 0.7 L
10 | 1 | 0.69979 |  | 1 | 1 | 0.69979
20 | 2 | 1.3996 |  | 2 | 2 | 1.3996
30 | 3 | 2.0994 |  | 3 | 3 | 2.0994
40 | 4 | 2.7992 |  | 4 | 4 | 2.7992
50 | 5 | 3.499 |  | 5 | 5 | 3.499
60 | 6 | 4.1987 |  | 6 | 6 | 4.1987
70 | 7 | 4.8985 |  | 7 | 7 | 4.8985
80 | 8 | 5.5983 |  | 8 | 8 | 5.5983
90 | 9 | 6.2981 |  | 9 | 9 | 6.2981
100 | 10 | 6.9979 |  | 10 | 10 | 6.9979
110 | 11 | 7.6977 |  | 11 | 11 | 7.6977
120 | 12 | 8.3975 |  | 12 | 12 | 8.3975
130 | 13 | 9.0973
140 | 14 | 9.7971
150 | 15 | 10.4969

## Procedure
Standard Procedure: add sludge, MgO & lime to jars all mixed together. Fill jars with composite mixture and start stir period, add coag while stirring at 200 rpm for 60s, add floc & let stir for 30s; reduce to 100 or 50 rpm for 2 mins, then let settle for 5 mins before collecting samples. (900 mL PW, 100 mL recirc, 30 mL lime, 15 mL MgO).
Slurry Procedure: Use same compostion for total blend (900 PW, 100 mL sludge recirc, 15 mL lime, 15 mL MgO) but prepared slurry mixture to consist of lime/MgO/sludge.. Kept same stir period and rates. Fill jars with 900 mL PW and stir at 200rpm. Add coag stir for 60s, add slurry mixture immediately followed by floc and let stir for 30s at 200rpm. Reduce rate to 100 or 50 rpm for 120s and then settle for 5 min before sampling.
NOTE:
2490 is CLAR 2537A
1580 is CLAR17650

## Input Settling Rate Data
Comment | Tap | total Vol | Settling heights (1000 mL Grad cylinder)
|  |  | 30 | 60 | 90 | 120 (2 min) | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) | 5:30 (min) | 360 (6 min) | 6:30 (min) | 420 (7 min) | 7:30 (min) | 480 (8 min) | 8:30 (min) | 540 (9 min) | 9:30 (min) | 600 (10 min) | 10:30 (min) | 11:00 (min)
|  |  |  | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)
[5 empty] | 30 | 60 | 90 | 120 | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)
| 0 ppm:blank 0 ppm:blank | 945 | 930 | 920 |  | 600 | 550 |  | 350 | 300 | 300 | 290 |  | 275 |  | 255 |  | 240 |  | 230 |  | 220
| 30 ppm:2537A 0.5 ppm:8181 | 965 |  | 900 | 800 | 750 | 640 |  | 450 | 370 | 360 | 345 | 330 |  | 310 |  | 280 |  | 265 |  | 250 |  | 235
| 20 ppm:2537A 0.5 ppm:8181 | 965 |  |  | 880 | 750 | 700 |  | 450 | 390 | 360 | 350 | 345 | 330 |  | 305 |  | 280 |  | 265 |  | 250 |  | 240
| 15 ppm:2537A 0.5 ppm:8181 | 975 | 900 | 850 | 770 | 690 | 600 | 500 | 370 | 360 | 350 | 345 |  | 330 |  | 295 |  | 275 |  | 260 |  | 250
| 15 ppm:2537A 1 ppm:8181 | 980 |  | 920 | 800 | 730 | 700 | 550 | 450 | 370 | 360 | 350 | 345 |  | 320 |  | 290 |  | 275 |  | 260 |  | 250
| 15 ppm:2537A 1.5 ppm:8181 | 965 |  |  | 870 | 800 | 750 | 670 | 550 | 370 | 370 | 360 | 355 | 340 |  | 315 |  | 295 |  | 275 |  | 260 |  | 250
| 15 ppm:1580 1 ppm:8181 | 980 | 900 | 800 | 650 | 550 | 425 | 360 | 365 | 360 | 355 | 345 |  | 330 |  | 310 |  | 290 |  | 275 |  | 265
| 15 ppm:8105 1 ppm:8181 | 960 |  | 900 | 750 | 650 | 500 | 450 | 390 | 380 | 375 | 365 | 360 |  | 335 |  | 310 |  | 295 |  | 280 |  | 270
| 15 ppm:1580 1 ppm:7878 | 960 |  |  | 850 | 750 | 600 | 480 | 420 | 400 | 385 | 370 | 355 | 340 |  | 320 |  | 300 |  | 285 |  | 275 |  | 265
| 15 ppm:8105 1 ppm:7878 | 965 | 880 | 720 | 630 | 520 | 440 | 420 | 400 | 380 | 365 | 350 |  | 330 |  | 310 |  | 290 |  | 280 |  | 270
| 15 ppm:1580 1 ppm:61610 | 970 |  | 900 | 820 | 710 | 600 | 500 | 410 | 385 | 380 | 370 | 360 |  | 340 |  | 320 |  | 300 |  | 285 |  | 270
| 15 ppm:8105 1 ppm:61610 | 955 |  |  | 900 | 800 | 700 | 600 | 510 | 400 | 390 | 380 | 370 | 360 |  | 340 |  | 320 |  | 300 |  | 285 |  | 270

## settling copy
PLOTTED DATA
Experiment | Jar | Settling heights (1000 mL Grad cylinder) | [15 empty] | Slope (600 s) | R^2 (600s) | Slope (300 s) | R^2 (300s) | Slope (180 s) | R^2 (180s) | Slope (60-150) | R^2 (60 - 150s) | 10 min Rate (ml/min) | RANK | 5 min Rate (ml/min) | RANK | 3 min Rate (ml/min) | RANK | 60-150 s Rate (ml/min) | RANK
|  | 0 | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 | 360 | 420 | 480 | 540 | 600
Exp 19 | 15 ppm:2537A 1 ppm:8181 | 980 | 920 | 800 | 730 | 700 | 550 | 450 | 370 | 360 | 350 | 345 | 320 | 290 | 275 | 260 | 250
| 15 ppm:17650 1 ppm:8181 | 980 | 900 | 800 | 650 | 550 | 425 | 360 | 365 | 360 | 355 | 345 | 330 | 310 | 290 | 275 | 265
| 15 ppm:18114 1 ppm:8181 | 960 | 900 | 750 | 650 | 500 | 450 | 390 | 380 | 375 | 365 | 360 | 335 | 310 | 295 | 280 | 270
| 15 ppm:17650 1 ppm:7878 | 960 | 850 | 750 | 600 | 480 | 420 | 400 | 385 | 370 | 355 | 340 | 320 | 300 | 285 | 275 | 265
| 15 ppm:18114 1 ppm:7878 | 965 | 880 | 720 | 630 | 520 | 440 | 420 | 400 | 380 | 365 | 350 | 330 | 310 | 290 | 280 | 270
| 15 ppm:17650 1 ppm:61610 | 970 | 900 | 820 | 710 | 600 | 500 | 410 | 385 | 380 | 370 | 360 | 340 | 320 | 300 | 285 | 270
| 15 ppm:18114 1 ppm:61610 | 955 | 900 | 800 | 700 | 600 | 510 | 400 | 390 | 380 | 370 | 360 | 340 | 320 | 300 | 285 | 270

## July 2022
PHASE F JAR TESTING
Date | Test | procedure | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | Trub % decrease | RANK | MAX | MIN | RANGE | Comment
2022-07-19 | 1 | standard 200 rpm & 100 rpm, 5 min settling | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 651 | 0% | 6 | 651 | 260 | 391 | J3 larger particle during stir & more FW. Settling rates are all very similar. Let settle for 5 mins. The water clarity in J3 was terrible.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 260 | 60.06% | 1
|  |  | 3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 549 | 15.67% | 4
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 557 | 14.44% | 5
|  |  | 5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 408 | 37.33% | 3
|  |  | 6 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 290 | 55.45% | 2
2022-07-19 | 2 | standard 200 rpm & 100 rpm, 5 min settling | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 847 | 0% | 6 | 847 | 96.7 | 750.3 | J6 looks the best with high clarity and lots of FW during stir. All jars have same particle size. J 6 settled the fastest and the other jars were about the same.
|  |  | 2 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 310 | 63.4% | 5
|  |  | 3 | 8181 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:8181 | 186 | 78.04% | 3
|  |  | 4 | 8181 | 1 | 1580 | 25 | 25 ppm:1580 1 ppm:8181 | 96.7 | 88.58% | 1
|  |  | 5 | 8181 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:8181 | 121 | 85.71% | 2
|  |  | 6 | 3058 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:3058 | 206 | 75.68% | 4
2022-07-20 | 3 | slurry method - 200 & 100 rpm | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 765 | 0% | 6 | 765 | 108 | 657 | No partciles with coag addition. J3 shows best flocs and it settles faster but the water clarity is not great. The other jars all settled about the same rate.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 246 | 67.84% | 4
|  |  | 3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 290 | 62.09% | 5
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 197 | 74.25% | 2
|  |  | 5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 243 | 68.24% | 3
|  |  | 6 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 108 | 85.88% | 1
2022-07-20 | 4 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 776 | 0% | 6 | 776 | 97.6 | 678.4 | all jars with coag didn't give any initial particle formation. The addition of floc showed good growth and J6 had the best size. Lots of FW during the stir period for J6. J6 showed fastest settling rate. Next J2 through J5 so the increase in coag actually decreased the settling rate with 1580.
|  |  | 2 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 260 | 66.49% | 5
|  |  | 3 | 8181 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:8181 | 163 | 78.99% | 4
|  |  | 4 | 8181 | 1 | 1580 | 25 | 25 ppm:1580 1 ppm:8181 | 143 | 81.57% | 3
|  |  | 5 | 8181 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:8181 | 97.6 | 87.42% | 1
|  |  | 6 | 3058 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:3058 | 127 | 83.63% | 2
2022-07-20 | 5 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 525 | 0% | 6 | 525 | 72.1 | 452.9 | very similar observations as exp 4. CXP3058 gives a better particle size than 8181 but water clarity doesn't finish as well. Less pin floc with 2537A vs 1580.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 124 | 76.38% | 5
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 105 | 80% | 4
|  |  | 4 | 8181 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:8181 | 95.5 | 81.81% | 2
|  |  | 5 | 8181 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:8181 | 72.1 | 86.27% | 1
|  |  | 6 | 3058 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:3058 | 104 | 80.19% | 3
2022-07-20 | 6 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 545 | 0% | 6 | 545 | 60.5 | 484.5 | addition of 18114 did give a cloudier mixture than previous coags and it increase with more coag. Particle size was biggest with cxp3058. settling rate J6>J2>j3>j4>j5
|  |  | 2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 174 | 68.07% | 5
|  |  | 3 | 8181 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:8181 | 92.2 | 83.08% | 4
|  |  | 4 | 8181 | 1 | 18114 | 25 | 25 ppm:18114 1 ppm:8181 | 81.2 | 85.1% | 3
|  |  | 5 | 8181 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:8181 | 70.6 | 87.05% | 2
|  |  | 6 | 3058 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:3058 | 60.5 | 88.9% | 1
2022-07-20 | 7 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 472 | 0% | 6 | 472 | 60.1 | 411.9 | there is an increase in FW as dosage increase. Not much of a noticeable change in floc size. J6>j5>j4>j3>j2>j1 for settling rates
|  |  | 2 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 248 | 47.46% | 5
|  |  | 3 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 158 | 66.53% | 4
|  |  | 4 | 8181 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:8181 | 119 | 74.79% | 3
|  |  | 5 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 63 | 86.65% | 2
|  |  | 6 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 60.1 | 87.27% | 1
2022-07-20 | 8 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 393 | 0% | 5 | 520 | 90.3 | 429.7 | same obs as exp 7
|  |  | 2 | 8181 | 0.5 | 1580 | 10 | 10 ppm:1580 0.5 ppm:8181 | 520 | -32.32% | 6
|  |  | 3 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 240 | 38.93% | 4
|  |  | 4 | 8181 | 1.5 | 1580 | 10 | 10 ppm:1580 1.5 ppm:8181 | 141 | 64.12% | 3
|  |  | 5 | 8181 | 2 | 1580 | 10 | 10 ppm:1580 2 ppm:8181 | 103 | 73.79% | 2
|  |  | 6 | 8181 | 2.5 | 1580 | 10 | 10 ppm:1580 2.5 ppm:8181 | 90.3 | 77.02% | 1
2022-07-20 | 9 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 0% | 6 | 999 | 168 | 831 | same obs as exp 7, no big effect with coag but doasge is low.
|  |  | 2 | 8181 | 0.5 | 18114 | 10 | 10 ppm:18114 0.5 ppm:8181 | 873 | 12.61% | 5
|  |  | 3 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 539 | 46.05% | 4
|  |  | 4 | 8181 | 1.5 | 18114 | 10 | 10 ppm:18114 1.5 ppm:8181 | 346 | 65.37% | 3
|  |  | 5 | 8181 | 2 | 18114 | 10 | 10 ppm:18114 2 ppm:8181 | 340 | 65.97% | 2
|  |  | 6 | 8181 | 2.5 | 18114 | 10 | 10 ppm:18114 2.5 ppm:8181 | 168 | 83.18% | 1
2022-07-21 | 10 | slurry method | 1 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 141 | 0% | 6 | 141 | 31.1 | 109.9 | J3 looks the best with large particles and lots of FW even during both stir periods. Particle size largest J5<J1<J6<J2<J4<J3. settling rate 16>15>24>25>31>38 for j4>j3>j1>j2>j5>j6. j6 finished the best with water clarity
|  |  | 2 | 7878 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7878 | 57.5 | 59.22% | 2
|  |  | 3 | 7767 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7767 | 82.9 | 41.21% | 4
|  |  | 4 | 3058 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3058 | 134 | 4.965% | 5
|  |  | 5 | 3090 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3090 | 73.6 | 47.8% | 3
|  |  | 6 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 31.1 | 77.94% | 1
2022-07-21 | 11 | slurry method | 1 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 115 | 0% | 3 | 277 | 43.1 | 233.9 | very similar trend with particle size as exp 10. J3 lots of FW. J4 15, J3 16, j1 24, j6 27, then j2 and J5. water clarity looks best in J6.
|  |  | 2 | 7878 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7878 | 166 | -44.35% | 4
|  |  | 3 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 183 | -59.13% | 5
|  |  | 4 | 3058 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:3058 | 277 | -140.9% | 6
|  |  | 5 | 3090 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:3090 | 106 | 7.826% | 2
|  |  | 6 | 61610 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:61610 | 43.1 | 62.52% | 1
2022-07-21 | 12 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 404 | 0% | 6 | 404 | 99.9 | 304.1 | very good dosage response, with large particle size and lots of FW. Settling rate is j6>j5>j4>j3>j2>j1
|  |  | 2 | 3058 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:3058 | 327 | 19.06% | 5
|  |  | 3 | 3058 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:3058 | 302 | 25.25% | 4
|  |  | 4 | 3058 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:3058 | 204 | 49.5% | 3
|  |  | 5 | 3058 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:3058 | 137 | 66.09% | 2
|  |  | 6 | 3058 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:3058 | 99.9 | 75.27% | 1
2022-07-21 | 13 | slurry | 1 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 39 | 0% | 3 | 121 | 31.9 | 89.1 | good particle growth with increased floc. Settling rate increased likewise and all faster than settling rates for J4-6. no difference between J4-J6. collected at 3 min mark.
|  |  | 2 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 52.9 | -35.64% | 4
|  |  | 3 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 121 | -210.3% | 6
|  |  | 4 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 65.8 | -68.72% | 5
|  |  | 5 | 61610 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:61610 | 34.8 | 10.77% | 2
|  |  | 6 | 61610 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:61610 | 31.9 | 18.21% | 1
2022-08-03 | 14 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 322 | 0% | 6 | 322 | 43.1 | 278.9 | J3 & J5 has the most FW during stir, particle size looks smallest in J6. settling rates for J2-J5 very similar, J6 is the slowest. Collect at 3 min.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 108 | 66.46% | 5
|  |  | 3 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 96 | 70.19% | 4
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 91.4 | 71.61% | 3
|  |  | 5 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 43.1 | 86.61% | 1
|  |  | 6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 60.4 | 81.24% | 2
2022-08-03 | 15 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 371 | 0% | 6 | 371 | 77.3 | 293.7 | 18114 gives cloudiness and it increases with dosgae increase. More floc larger particles & faster settling. The settling rate does seem to slow with more coag. Much better water clarity with increased coag. Sludge bed is less compact with high coag, 150 mL at 30 ppm, 125 at 20 and 120 at 15.
|  |  | 2 | 8181 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:8181 | 104 | 71.97% | 3
|  |  | 3 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 116 | 68.73% | 4
|  |  | 4 | 8181 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:8181 | 129 | 65.23% | 5
|  |  | 5 | 8181 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:8181 | 100 | 73.05% | 2
|  |  | 6 | 8181 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:8181 | 77.3 | 79.16% | 1
2022-08-03 | 16 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 552 | 0% | 6 | 552 | 40.7 | 511.3 | same cloudiness. But no diff in particle size. J2 fastest settling, followed by J3. no diff in settling between J4-J6. no difference in sludge compaction
|  |  | 2 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 60.7 | 89% | 3
|  |  | 3 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 65.5 | 88.13% | 4
|  |  | 4 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 95 | 82.79% | 5
|  |  | 5 | 61610 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:61610 | 43.4 | 92.14% | 2
|  |  | 6 | 61610 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:61610 | 40.7 | 92.63% | 1
2022-08-03 | 17 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 346 | 0% | 6 | 346 | 37.6 | 308.4 | excellent response with Lrger particle as floc increases, coag doesn't affect size. Lots of FW in all jars. Much faster settling rate with 7878 over other flocs. J2>J3>J4>J5>J6…more coags slows settling slightly.
|  |  | 2 | 7878 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:7878 | 37.6 | 89.13% | 1
|  |  | 3 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 52.8 | 84.74% | 3
|  |  | 4 | 7878 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:7878 | 88 | 74.57% | 5
|  |  | 5 | 7878 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:7878 | 64.8 | 81.27% | 4
|  |  | 6 | 7878 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:7878 | 45 | 86.99% | 2
2022-08-03 | 18 | settling test - use slurry procedure with 20% sludge | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 533 | 0% | 6 | 533 | 151 | 382 | no particle size growth difference bt the jars. J4-6 had the same particel size. There is a slight increase in settling rate with more floc. 5 min settling
|  |  | 2 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 151 | 71.67% | 1
|  |  | 3 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 172 | 67.73% | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 425 | 20.26% | 5
|  |  | 5 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 318 | 40.34% | 3
|  |  | 6 | 8181 | 1.5 | 2537A | 15 | 15 ppm:2537A 1.5 ppm:8181 | 332 | 37.71% | 4
2022-08-03 | 19 | settling test - use slurry procedure with 20% sludge | 1 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 541 | 0% | 6 | 541 | 132 | 409 | 18114 jars all showed a particulate formation but not 1580. j4 looked the best during the stir period. 7878 jars showed the fastest settling
|  |  | 2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 522 | 3.512% | 5
|  |  | 3 | 7878 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:7878 | 305 | 43.62% | 4
|  |  | 4 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 147 | 72.83% | 2
|  |  | 5 | 61610 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:61610 | 216 | 60.07% | 3
|  |  | 6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 132 | 75.6% | 1
2022-08-03 | 20 | settling test - use slurry procedure with 20% sludge | 1 | 8181 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A | 0 | 0 | 0
|  |  | 2 | 8181 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 3 | 8181 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 5 | 8181 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 6 | 8181 | 1.5 | 18114 | 30 | 30 ppm:18114 1.5 ppm:8181 |  | #DIV/0! | #N/A

## Exp 1 & 3
Jar | Flocculant | Floc ppm | Coagulant | Coag ppm | Chemicals | NTU
1 | blank | 0 | blank | 0 | blank | 651
2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 260
3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 549
4 | 8181 | 1 | 8105 | 15 | 15 ppm:8105 1 ppm:8181 | 557
5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 408
6 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 290
1 | blank | 0 | blank | 0 | blank | 765
2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 246
3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 290
4 | 8181 | 1 | 8105 | 15 | 15 ppm:8105 1 ppm:8181 | 197
5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 243
6 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 108
Exp 3 - 8181 coag screen (slurry method)
Exp 1 - 8181 coag screen (standard method)

## Exp 2 & 4
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank | 0 | blank | 0 | Blank | 847
2 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 310
3 | 8181 | 1 | 17650 | 20 | 20 ppm:17650 1 ppm:8181 | 186
4 | 8181 | 1 | 17650 | 25 | 25 ppm:17650 1 ppm:8181 | 96.7
5 | 8181 | 1 | 17650 | 30 | 30 ppm:17650 1 ppm:8181 | 121
6 | 3058 | 1 | 17650 | 30 | 30 ppm:17650 1 ppm:3058 | 206
1 | blank | 0 | blank | 0 | Blank | 776
2 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 260
3 | 8181 | 1 | 17650 | 20 | 20 ppm:17650 1 ppm:8181 | 163
4 | 8181 | 1 | 17650 | 25 | 25 ppm:17650 1 ppm:8181 | 143
5 | 8181 | 1 | 17650 | 30 | 30 ppm:17650 1 ppm:8181 | 97.6
6 | 3058 | 1 | 17650 | 30 | 30 ppm:17650 1 ppm:3058 | 127
Exp 4 - 8181 & 1580 (slurry method)
Exp 2 - 8181 & 1580 (standard method)

## Exp 3 & 14
Jar | Flocculant | Floc ppm | Coagulant | Coag ppm | Chemicals | NTU | % Decrease
1 | blank | 0 | blank | 0 | Blank | 765 | 0%
2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537 1 ppm:8181 | 246 | 67.84%
3 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 197 | 74.25%
4 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 243 | 68.24%
5 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 108 | 85.88%
1 | blank | 0 | blank | 0 | Blank | 322 | 0%
2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537 1 ppm:8181 | 108 | 66.46%
3 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 96 | 70.19%
4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 91.4 | 71.61%
5 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 43.1 | 86.61%
6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 60.4 | 81.24%
Exp 14 - Aug 3
Exp 3 - July 21

## Exp 4-6 coag profile w 8181
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | #REF! | 0 | Blank |  | 0 |  | 0
1 | blank | 0 | blank | 0 | Blank | 776 | 0%
2 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 260 | 66.49%
3 | 8181 | 1 | 17650 | 20 | 20 ppm:17650 1 ppm:8181 | 163 | 78.99%
4 | 8181 | 1 | 17650 | 25 | 25 ppm:17650 1 ppm:8181 | 143 | 81.57%
5 | 8181 | 1 | 17650 | 30 | 30 ppm:17650 1 ppm:8181 | 97.6 | 87.42%
1 | blank | 0 | blank | 0 | Blank | 525 | 0%
2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537 1 ppm:8181 | 124 | 76.38%
3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 105 | 80%
4 | 8181 | 1 | 2537A | 25 | 25 ppm:2537 1 ppm:8181 | 95.5 | 81.81%
5 | 8181 | 1 | 2537A | 30 | 30 ppm:2537 1 ppm:8181 | 72.1 | 86.27%
1 | blank | 0 | blank | 0 | Blank | 545 | 0%
2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 174 | 68.07%
3 | 8181 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:8181 | 92.2 | 83.08%
4 | 8181 | 1 | 18114 | 25 | 25 ppm:18114 1 ppm:8181 | 81.2 | 85.1%
5 | 8181 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:8181 | 70.6 | 87.05%
Reset Set-Jar Order

## Exp 7-9 8181 Profile
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | #REF! | 0 | Blank |  | 0 |  | 0
1 | blank | 0 | blank | 0 | Blank | 472 | 0%
2 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537 0.5 ppm:8181 | 248 | 47.46%
3 | 8181 | 1 | 2537A | 10 | 10 ppm:2537 1 ppm:8181 | 158 | 66.53%
4 | 8181 | 1.5 | 2537A | 10 | 10 ppm:2537 1.5 ppm:8181 | 119 | 74.79%
5 | 8181 | 2 | 2537A | 10 | 10 ppm:2537 2 ppm:8181 | 63 | 86.65%
6 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537 2.5 ppm:8181 | 60.1 | 87.27%
1 | blank | 0 | blank | 0 | Blank | 393 | 0%
2 | 8181 | 0.5 | 17650A | 10 | 10 ppm:17650A 0.5 ppm:8181 | 520 | -32.32%
3 | 8181 | 1 | 17650A | 10 | 10 ppm:17650A 1 ppm:8181 | 240 | 38.93%
4 | 8181 | 1.5 | 17650A | 10 | 10 ppm:17650A 1.5 ppm:8181 | 141 | 64.12%
5 | 8181 | 2 | 17650A | 10 | 10 ppm:17650A 2 ppm:8181 | 103 | 73.79%
6 | 8181 | 2.5 | 17650A | 10 | 10 ppm:17650A 2.5 ppm:8181 | 90.3 | 77.02%
1 | blank | 0 | blank | 0 | Blank | 999 | 0%
2 | 8181 | 0.5 | 18114 | 10 | 10 ppm:18114 0.5 ppm:8181 | 873 | 12.61%
3 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 539 | 46.05%
4 | 8181 | 1.5 | 18114 | 10 | 10 ppm:18114 1.5 ppm:8181 | 346 | 65.37%
5 | 8181 | 2 | 18114 | 10 | 10 ppm:18114 2 ppm:8181 | 340 | 65.97%
6 | 8181 | 2.5 | 18114 | 10 | 10 ppm:18114 2.5 ppm:8181 | 168 | 83.18%
Reset Set-Jar Order

## Exp 10-11 Flocs w 1580 vs 8105
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 141 | 0%
2 | 7878 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7878 | 57.5 | 59.22%
3 | 7767 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7767 | 82.9 | 41.21%
4 | 3058 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3058 | 134 | 4.965%
5 | 3090 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3090 | 73.6 | 47.8%
6 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 31.1 | 77.94%
1 | 8181 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:8181 | 115 | 0%
2 | 7878 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:7878 | 166 | -44.35%
3 | 7767 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:7767 | 183 | -59.13%
4 | 3058 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:3058 | 277 | -140.9%
5 | 3090 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:3090 | 106 | 7.826%
6 | 61610 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:61610 | 43.1 | 62.52%
Exp 11 - Floc screen w/ 17650
Exp 10 - Floc screen w/ 18114

## Exp 7 vs 12
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | blank | 0 | blank | 0 | Blank | 472 | 0%
2 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 248 | 47.46%
3 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 158 | 66.53%
4 | 8181 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:8181 | 119 | 74.79%
5 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 63 | 86.65%
6 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 60.1 | 87.27%
1 | blank | 0 | blank | 0 | Blank | 404 | 0%
2 | 3058 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:3058 | 327 | 19.06%
3 | 3058 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:3058 | 302 | 25.25%
4 | 3058 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:3058 | 204 | 49.5%
5 | 3058 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:3058 | 137 | 66.09%
6 | 3058 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:3058 | 99.9 | 75.27%
Exp 12 - 3058 w/ 2537A
Exp 7 - 8181 w/ 2537A

## Exp 13
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 121 | 0%
2 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 52.9 | -35.64%
3 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 39 | -210.3%
4 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 65.8 | -68.72%
5 | 61610 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:61610 | 34.8 | 10.77%
6 | 61610 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:61610 | 31.9 | 18.21%
Exp 13 - Dosage Profile 6161 & 18114

## Exp 15-17 Dosage Profile
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
1 | #REF! | 0 | Blank |  | 0 |  | 0
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 371 | 0%
2 | 8181 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:8181 | 104 | 71.97%
3 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 116 | 68.73%
4 | 8181 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:8181 | 129 | 65.23%
5 | 8181 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:8181 | 100 | 73.05%
6 | 8181 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:8181 | 77.3 | 79.16%
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 552 | 0%
2 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 60.7 | 89%
3 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 65.5 | 88.13%
4 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 95 | 82.79%
5 | 61610 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:61610 | 43.4 | 92.14%
6 | 61610 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:61610 | 40.7 | 92.63%
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 346 | 0%
2 | 7878 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:7878 | 37.6 | 89.13%
3 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 52.8 | 84.74%
4 | 7878 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:7878 | 88 | 74.57%
5 | 7878 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:7878 | 64.8 | 81.27%
6 | 7878 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:7878 | 45 | 86.99%
Reset Set-Jar Order

## Exp 19
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU | % Decrease
| 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 318
1 | 8181 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:8181 | 541 | 0%
2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 522 | 3.512%
3 | 7878 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:7878 | 305 | 43.62%
4 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 147 | 72.83%
5 | 61610 | 1 | 17650 | 15 | 15 ppm:17650 1 ppm:61610 | 216 | 60.07%
6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 132 | 75.6%
Exp 19 - Settling Test