## Blend Ratio
Plant Baseline | Rate |  | % composition | Normalized to 1000 mL | x7 | normalize 700 ml
WLS Streams |  | outlet | 927
De-oiled Water | 820 |  | 88.4574 | 884.5739 | 6192.0173 | 619.2017
HLS Sludge | 75 |  | 8.0906 | 80.9061 | 566.343 | 56.6343
Low Pressure BD | 0 |  | 0 | 0 | 0 | 0
Make up Water | 0 |  | 0 | 0 | 0 | 0
Lime | 16 |  | 1.726 | 17.26 | 120.8198 | 12.082
Mag | 16 |  | 1.726 | 17.26 | 120.8198 | 12.082
| 927 |  | 100 | 1000 | 7000 | 700
| 1% | 0.1%
ppm | 10000 | 1000
1 mL in 1L | 10 | 1
1 mL in .7 L | 14.2857 | 1.4286
required dosage (ppm) | 80 | 8
# mL in 1L | 8 | 8
# mL in 0.7 L | 5.6 | 5.6
required dosage (ppm) | # mL in 1L | # mL in 0.7 L |  | required dosage (ppm) | # mL in 1L | # mL in 0.7 L
10 | 1 | 0.69979 |  | 1 | 1 | 0.69979
20 | 2 | 1.3996 |  | 2 | 2 | 1.3996
30 | 3 | 2.0994 |  | 3 | 3 | 2.0994
40 | 4 | 2.7992 |  | 4 | 4 | 2.7992
50 | 5 | 3.499 |  | 5 | 5 | 3.499
60 | 6 | 4.1987 |  | 6 | 6 | 4.1987
70 | 7 | 4.8985 |  | 7 | 7 | 4.8985
80 | 8 | 5.5983 |  | 8 | 8 | 5.5983
90 | 9 | 6.2981 |  | 9 | 9 | 6.2981
100 | 10 | 6.9979 |  | 10 | 10 | 6.9979
110 | 11 | 7.6977 |  | 11 | 11 | 7.6977
120 | 12 | 8.3975 |  | 12 | 12 | 8.3975
130 | 13 | 9.0973
140 | 14 | 9.7971
150 | 15 | 10.4969

## Procedure
Composite or standard procedure: prepare composite sample with produced water, sludge, MgO & lime all mixed together. Fill jars and add coag while stirring at 200 rpm for 60s, add floc & let stir for 30s, reduce to 100 rpm for 2 mins, then let settle for 5 mins before collecting samples.
NOTE:
2490 is CLAR 2537A
1580 is CLAR17650
2531 is CL flco
1252 is CL Coag

## March 2022
PHASE E JAR TESTING
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
3-23-2022 |  | 1 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 228 | 6 | 228 | 106 | 122 | J6, J5 settled fastest. During stirring J6 lookedd to have more FW. They all look garbage wrt clarity
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 115 | 2
|  |  | 3 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 106 | 1
|  |  | 4 | 7767 | 0.5 | 8190 | 20 | 20 ppm:8190 0.5 ppm:7767 | 137 | 4
|  |  | 5 | 7767 | 0.5 | 1580 | 20 | 20 ppm:1580 0.5 ppm:7767 | 146 | 5
|  |  | 6 | 7767 | 0.5 | 8105 | 20 | 20 ppm:8105 0.5 ppm:7767 | 126 | 3
3-23-2022 |  | 2 | 1 | cl20f | 0.5 | cl20c | 20 | 20 ppm:cl20c 0.5 ppm:cl20f | 375 | 6 | 375 | 47.2 | 327.8 | J2 is the only jar with FW and it has the largest partcile size. J2>j1>J4>j6>5>j3 order of settling rates.
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 47.2 | 1
|  |  | 3 | 7878 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7878 | 53.4 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 87.1 | 3
|  |  | 5 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 261 | 5
|  |  | 6 | 7757 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7757 | 224 | 4
3-24-2022 |  | 3 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 304 | 6 | 304 | 108 | 196
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 185 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 162 | 4
|  |  | 4 | 8181 | 0.5 | 2537A | 40 | 40 ppm:2537A 0.5 ppm:8181 | 120 | 2
|  |  | 5 | 8181 | 0.5 | 2537A | 50 | 50 ppm:2537A 0.5 ppm:8181 | 108 | 1
|  |  | 6 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 125 | 3
3-24-2022 |  | 4 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 214 | 6 | 214 | 43.5 | 170.5 | the increase floc did give larger particle size and there was more FW with the increase. Also the settling rate was linear with the increase. Water clarity is all over the place…need to repeat this experiment
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 105 | 2
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 168 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 43.5 | 1
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 143 | 3
3-24-2022 |  | 5 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 227 | 6 | 227 | 91.8 | 135.2 | repeat exp 4. same observations. 21s<25<28<32<48 is the settling times to get a defined slduge edge in jars ordered 6-1. J 6 settled fastest.
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 171 | 3
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 92.2 | 2
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 179 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 172 | 4
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 91.8 | 1
3-24-2022 |  | 6 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 213 | 6 | 213 | 24.3 | 188.7 | significaant improvement in the amount of FW at 5 ppm 8181. 17s< 21s was the settling times for J6 & J5. interestingly yhe settling times for J2< J3<J4 is in this order…less coag it settles faster???
|  |  | 2 | 8181 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:8181 | 181 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 151 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 166 | 4
|  |  | 5 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 159 | 3
|  |  | 6 | 8181 | 5 | 2537A | 10 | 10 ppm:2537A 5 ppm:8181 | 24.3 | 1
3-24-2022 |  | 7 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 210 | 6 | 210 | 36.5 | 173.5 | particle size increase with more floc & increase FW. J 6 w/o coag probably as the same amount of FW as J5 with coag. Seems like the coag is preventing improvement. J5 did settle faste than J6 but J6 was same rate as J4. The increase in floc did give faster settling. also visual improvement in water clarity
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 194 | 5
|  |  | 3 | 8181 | 4 | 2537A | 10 | 10 ppm:2537A 4 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 6 | 2537A | 10 | 10 ppm:2537A 6 ppm:8181 | 44.4 | 2
|  |  | 5 | 8181 | 8 | 2537A | 10 | 10 ppm:2537A 8 ppm:8181 | 36.5 | 1
|  |  | 6 | 8181 | 4 | 2537A | 0 | 0 ppm:2537A 4 ppm:8181 | 94.6 | 3
[10 empty] | #N/A | 67.9 | 21.3 | 46.6 | exp 7 turbs taken after first numbers were recorded so approx 10 min f settling
[9 empty] | 67.9 | 5
[9 empty] | 62.3 | 4
[9 empty] | 41.9 | 3
[9 empty] | 21.3 | 1
[9 empty] | 34.7 | 2
3-25-2022 |  | 8 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 221 | 6 | 221 | 45 | 176 | no obvious difference in size with increase in coag or amount of FW. Reverse trend with settling rate…its slower as coag increases. FLOC controls bed & particle size.
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 174 | 5
|  |  | 3 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 147 | 3
|  |  | 4 | 8181 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:8181 | 148 | 4
|  |  | 5 | 8181 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:8181 | 126 | 2
|  |  | 6 | 8181 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:8181 | 45 | 1
3-25-2022 |  | 9 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 196 | 4 | 321 | 127 | 194 | J4&J5 does look slightly better than the other jars during the stir period. J5>J6>J1>J3>j2 IN ORDER OF FASTEST SETTLING RATES. Note- MgO collected from phase G since it was plugged in phase E. Phase G uses PW in the slurry whereas Phase E uses soften brackish
|  |  | 2 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 179 | 2
|  |  | 3 | 8181 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:8181 | 127 | 1
|  |  | 4 | 8181 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:8181 | 321 | 6
|  |  | 5 | 8181 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:8181 | 194 | 3
|  |  | 6 | 8181 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:8181 | 261 | 5
3-25-2022 |  | 10 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 295 | 6 | 295 | 24.5 | 270.5 | same MgO issue as Exp 9. really nice trend in size & FW with the increase…visible sludge line at 21 s for J6 & J5, ~ 23s for J4, 26s for J3 & 35s for J2. So good settling response with more floc.
|  |  | 2 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 161 | 5
|  |  | 3 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 98.7 | 4
|  |  | 4 | 61610 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:61610 | 89.2 | 3
|  |  | 5 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 24.5 | 1
|  |  | 6 | 61610 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:61610 | 28.1 | 2
3-25-2022 |  | 11 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 286 | 6 | 286 | 34.3 | 251.7 | no change in size, but the FW was higher in J1 vs J6, in that order. settling rates were all comparable.
|  |  | 2 | 61610 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:61610 | 78.2 | 5
|  |  | 3 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 51.7 | 4
|  |  | 4 | 61610 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:61610 | 36.9 | 2
|  |  | 5 | 61610 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:61610 | 34.3 | 1
|  |  | 6 | 61610 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:61610 | 41.2 | 3
3-25-2022 |  | 12 | 1 | blank |  | blank |  | ppm:blank ppm:blank |  | #N/A | 0 | 0 | 0
|  |  | 2 | 61610 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:61610 |  | #N/A
|  |  | 3 | 61610 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:61610 |  | #N/A
|  |  | 4 | 61610 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:61610 |  | #N/A
|  |  | 5 | 61610 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:61610 |  | #N/A
|  |  | 6 | 61610 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:61610 |  | #N/A
|  | 14 | 1 | blank |  |  |  | ppm: ppm:blank |  | #N/A | 0 | 0 | 0
|  |  | 2 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 3 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 4 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 5 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 6 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  | 15 | 1 |  |  |  |  | ppm: ppm: |  | #N/A | 0 | 0 | 0
|  |  | 2 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 3 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 4 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 5 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 6 |  |  |  |  | ppm: ppm: |  | #N/A

## March 2022 - field version
PHASE E JAR TESTING
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
3-23-2022 |  | 1 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 228 | 6 | 228 | 106 | 122 | J6, J5 settled fastest. During stirring J6 lookedd to have more FW. They all look garbage wrt clarity
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 115 | 2
|  |  | 3 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 106 | 1
|  |  | 4 | 7767 | 0.5 | 8190 | 20 | 20 ppm:8190 0.5 ppm:7767 | 137 | 4
|  |  | 5 | 7767 | 0.5 | 1580 | 20 | 20 ppm:1580 0.5 ppm:7767 | 146 | 5
|  |  | 6 | 7767 | 0.5 | 8105 | 20 | 20 ppm:8105 0.5 ppm:7767 | 126 | 3
3-23-2022 |  | 2 | 1 | 2531 | 0.5 | 1252 | 20 | 20 ppm:1252 0.5 ppm:2531 | 375 | 6 | 375 | 47.2 | 327.8 | J2 is the only jar with FW and it has the largest partcile size. J2>j1>J4>j6>5>j3 order of settling rates.
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 47.2 | 1
|  |  | 3 | 7878 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7878 | 53.4 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 87.1 | 3
|  |  | 5 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 261 | 5
|  |  | 6 | 7757 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7757 | 224 | 4
3-24-2022 |  | 3 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 304 | 6 | 304 | 108 | 196
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 185 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 162 | 4
|  |  | 4 | 8181 | 0.5 | 2537A | 40 | 40 ppm:2537A 0.5 ppm:8181 | 120 | 2
|  |  | 5 | 8181 | 0.5 | 2537A | 50 | 50 ppm:2537A 0.5 ppm:8181 | 108 | 1
|  |  | 6 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 125 | 3
3-24-2022 |  | 4 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 214 | 6 | 214 | 43.5 | 170.5 | the increase floc did give larger particle size and there was more FW with the increase. Also the settling rate was linear with the increase. Water clarity is all over the place…need to repeat this experiment
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 105 | 2
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 168 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 43.5 | 1
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 143 | 3
3-24-2022 |  | 5 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 227 | 6 | 227 | 91.8 | 135.2 | repeat exp 4. same observations. 21s<25<28<32<48 is the settling times to get a defined slduge edge in jars ordered 6-1. J 6 settled fastest.
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 171 | 3
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 92.2 | 2
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 179 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 172 | 4
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 91.8 | 1
3-24-2022 |  | 6 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 213 | 6 | 213 | 24.3 | 188.7 | significaant improvement in the amount of FW at 5 ppm 8181. 17s< 21s was the settling times for J6 & J5. interestingly yhe settling times for J2< J3<J4 is in this order…less coag it settles faster???
|  |  | 2 | 8181 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:8181 | 181 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 151 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 166 | 4
|  |  | 5 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 159 | 3
|  |  | 6 | 8181 | 5 | 2537A | 10 | 10 ppm:2537A 5 ppm:8181 | 24.3 | 1
3-24-2022 |  | 7 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 210 | 6 | 210 | 36.5 | 173.5 | particle size increase with more floc & increase FW. J 6 w/o coag probably as the same amount of FW as J5 with coag. Seems like the coag is preventing improvement. J5 did settle faste than J6 but J6 was same rate as J4. The increase in floc did give faster settling. also visual improvement in water clarity
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 194 | 5
|  |  | 3 | 8181 | 4 | 2537A | 10 | 10 ppm:2537A 4 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 6 | 2537A | 10 | 10 ppm:2537A 6 ppm:8181 | 44.4 | 2
|  |  | 5 | 8181 | 8 | 2537A | 10 | 10 ppm:2537A 8 ppm:8181 | 36.5 | 1
|  |  | 6 | 8181 | 4 | 2537A | 0 | 0 ppm:2537A 4 ppm:8181 | 94.6 | 3
[10 empty] | #N/A | 67.9 | 21.3 | 46.6 | exp 7 turbs taken after first numbers were recorded so approx 10 min f settling
[9 empty] | 67.9 | 5
[9 empty] | 62.3 | 4
[9 empty] | 41.9 | 3
[9 empty] | 21.3 | 1
[9 empty] | 34.7 | 2
3-25-2022 |  | 8 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 221 | 6 | 221 | 45 | 176 | no obvious difference in size with increase in coag or amount of FW. Reverse trend with settling rate…its slower as coag increases. FLOC controls bed & particle size.
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 174 | 5
|  |  | 3 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 147 | 3
|  |  | 4 | 8181 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:8181 | 148 | 4
|  |  | 5 | 8181 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:8181 | 126 | 2
|  |  | 6 | 8181 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:8181 | 45 | 1
|  | 9 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 196 | 4 | 321 | 127 | 194 | J4&J5 does look slightly better than the other jars during the stir period. J5>J6>J1>J3>j2 IN ORDER OF FASTEST SETTLING RATES. Note- MgO collected from phase G since it was plugged in phase E. Phase G uses PW in the slurry whereas Phase E uses soften brackish
|  |  | 2 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 179 | 2
|  |  | 3 | 8181 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:8181 | 127 | 1
|  |  | 4 | 8181 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:8181 | 321 | 6
|  |  | 5 | 8181 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:8181 | 194 | 3
|  |  | 6 | 8181 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:8181 | 261 | 5
|  | 10 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 295 | 6 | 295 | 24.5 | 270.5 | same MgO issue as Exp 9. really nice trend in size & FW with the increase…visible sludge line at 21 s for J6 & J5, ~ 23s for J4, 26s for J3 & 35s for J2. So good settling response with more floc.
|  |  | 2 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 161 | 5
|  |  | 3 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 98.7 | 4
|  |  | 4 | 61610 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:61610 | 89.2 | 3
|  |  | 5 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 24.5 | 1
|  |  | 6 | 61610 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:61610 | 28.1 | 2
|  | 12 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 286 | 6 | 286 | 34.3 | 251.7 | no change in size, but the FW was higher in J1 vs J6, in that order. settling rates were all comparable.
|  |  | 2 | 61610 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:61610 | 78.2 | 5
|  |  | 3 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 51.7 | 4
|  |  | 4 | 61610 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:61610 | 36.9 | 2
|  |  | 5 | 61610 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:61610 | 34.3 | 1
|  |  | 6 | 61610 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:61610 | 41.2 | 3
|  | 13 | 1 | blank |  | blank |  | ppm:blank ppm:blank |  | #N/A | 0 | 0 | 0
|  |  | 2 | 61610 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:61610 |  | #N/A
|  |  | 3 | 61610 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:61610 |  | #N/A
|  |  | 4 | 61610 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:61610 |  | #N/A
|  |  | 5 | 61610 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:61610 |  | #N/A
|  |  | 6 | 61610 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:61610 |  | #N/A
|  | 14 | 1 | blank |  |  |  | ppm: ppm:blank |  | #N/A | 0 | 0 | 0
|  |  | 2 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 3 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 4 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 5 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  |  | 6 | 61610 |  |  |  | ppm: ppm:61610 |  | #N/A
|  | 15 | 1 |  |  |  |  | ppm: ppm: |  | #N/A | 0 | 0 | 0
|  |  | 2 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 3 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 4 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 5 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 6 |  |  |  |  | ppm: ppm: |  | #N/A

## March - PHASE E - 8 & 11
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 221
2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 174
3 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 147
4 | 8181 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:8181 | 148
5 | 8181 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:8181 | 126
6 | 8181 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:8181 | 45
5 | blank |  | blank |  | blank | 286
6 | 61610 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:61610 | 78.2
5 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 51.7
6 | 61610 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:61610 | 36.9
5 | 61610 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:61610 | 34.3
6 | 61610 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:61610 | 41.2
Exp 11 - 61610 w/ 2537A dosage profile
Exp 8 - 8181 w/ 2537A profileblank blank ppm:blank ppm:blank 286 61610 2 2537A 10 10 ppm:2537A 2 ppm:61610 78.2 61610 2 2537A 20 20 ppm:2537A 2 ppm:61610 51.7 61610 2 2537A 30 30 ppm:2537A 2 ppm:61610 36.9 61610 2 2537A 40 40 ppm:2537A 2 ppm:61610 34.3 61610 2 2537A 50 50 ppm:2537A 2 ppm:61610 41.2

## March - PHASE E - 5&10
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | ppm:blank ppm:blank | 227
2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 171
3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 92.2
4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 179
5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 172
6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 91.8
5 | blank |  | blank |  | ppm:blank ppm:blank | 295
6 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 161
5 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 98.7
6 | 61610 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:61610 | 89.2
5 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 24.5
6 | 61610 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:61610 | 28.1
Exp 10 - 61610 profile w/ 2537A
Exp 5 - 8181 profile w/ 2537A

## March - PHASE E - 1&9
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 196
2 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 179
3 | 8181 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:8181 | 127
4 | 8181 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:8181 | 321
5 | 8181 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:8181 | 194
6 | 8181 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:8181 | 261
5 | blank |  | blank |  | ppm:blank ppm:blank | 228
6 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 115
5 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 106
6 | 7767 | 0.5 | 8190 | 20 | 20 ppm:8190 0.5 ppm:7767 | 137
5 | 7767 | 0.5 | 1580 | 20 | 20 ppm:1580 0.5 ppm:7767 | 146
6 | 7767 | 0.5 | 8105 | 20 | 20 ppm:8105 0.5 ppm:7767 | 126
Exp 1 - 7767 coag screen
Exp 9 - 8181 coag screen

## March - PHASE E - 3&8
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 221
2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 174
3 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 147
4 | 8181 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:8181 | 148
5 | 8181 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:8181 | 126
6 | 8181 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:8181 | 45
1 | blank |  | blank |  | blank | 304
2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 185
3 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 162
4 | 8181 | 0.5 | 2537A | 40 | 40 ppm:2537A 0.5 ppm:8181 | 120
5 | 8181 | 0.5 | 2537A | 50 | 50 ppm:2537A 0.5 ppm:8181 | 108
6 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 125
Exp 3 - Low 8181 w/ 2537A dosage profile
Exp 8 - High 8181 w/ 2537A dosage profile

## March - PHASE E - 6&7
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | ppm:blank ppm:blank | 213
2 | 8181 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:8181 | 181
3 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 151
4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 166
5 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 159
6 | 8181 | 5 | 2537A | 10 | 10 ppm:2537A 5 ppm:8181 | 24.3
5 | blank |  | blank |  | ppm:blank ppm:blank | 210
6 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 194
5 | 8181 | 4 | 2537A | 10 | 10 ppm:2537A 4 ppm:8181 | 159
6 | 8181 | 6 | 2537A | 10 | 10 ppm:2537A 6 ppm:8181 | 44.4
5 | 8181 | 8 | 2537A | 10 | 10 ppm:2537A 8 ppm:8181 | 36.5
6 | 8181 | 4 | 2537A | 0 | 0 ppm:2537A 4 ppm:8181 | 94.6
Exp 7 - High 8181 dosage profile w/ min 2537A
Exp 6 - Low vs high 8181 w/ low 2537A

## March - PHASE E - 4&5
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 214
2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 105
3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 159
4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 168
5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 43.5
6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 143
5 | blank |  | blank |  | blank | 227
6 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 171
5 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 92.2
6 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 179
5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 172
6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 91.8
Exp 5 - 8181 dosage profile w/ 2537A
Exp 4 - 8181 dosage profile w/ 2537A

## March - PHASE E - 3&4
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 304
2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 185
3 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 162
4 | 8181 | 0.5 | 2537A | 40 | 40 ppm:2537A 0.5 ppm:8181 | 120
5 | 8181 | 0.5 | 2537A | 50 | 50 ppm:2537A 0.5 ppm:8181 | 108
6 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 125
Exp 3 - 8181 w/ 2537A dosage profile

## March - PHASE E 1&2
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | Blank | 228
2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 115
3 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 106
4 | 7767 | 0.5 | 8190 | 20 | 20 ppm:8190 0.5 ppm:7767 | 137
5 | 7767 | 0.5 | 1580 | 20 | 20 ppm:1580 0.5 ppm:7767 | 146
6 | 7767 | 0.5 | 8105 | 20 | 20 ppm:8105 0.5 ppm:7767 | 126
5 | cl20f | 0.5 | cl20c | 20 | 20 ppm:cl20c 0.5 ppm:cl20f | 375
6 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 47.2
5 | 7878 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7878 | 53.4
6 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 87.1
5 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 261
6 | 7757 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7757 | 224
Exp 2 - Floc Screen
Exp 1 - Coag Screen

## Settling Data Input
Comment | Tap | total Vol | Settling heights (1000 mL Grad cylinder)
|  |  | 30 | 60 | 90 | 120 (2 min) | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) | 5:30 (min) | 360 (6 min) | 6:30 (min) | 420 (7 min) | 7:30 (min) | 480 (8 min) | 8:30 (min) | 540 (9 min) | 9:30 (min) | 600 (10 min) | 10:30 (min) | 11:00 (min)
|  |  |  | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)
[5 empty] | 30 | 60 | 90 | 120 | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)