## Procedure
Standard Procedure: add sludge, MgO & lime to jars all mixed together. Fill jars with composite mixture and start stir period, add coag while stirring at 200 rpm for 60s, add floc & let stir for 30s; reduce to 100 or 50 rpm for 2 mins, then let settle for 5 mins before collecting samples. (900 mL PW, 100 mL recirc, 30 mL lime, 15 mL MgO).
Slurry Procedure: Use same compostion for total blend (900 PW, 100 mL sludge recirc, 15 mL lime, 15 mL MgO) but prepared slurry mixture to consist of lime/MgO/sludge.. Kept same stir period and rates. Fill jars with 900 mL PW and stir at 200rpm. Add coag stir for 60s, add slurry mixture immediately followed by floc and let stir for 30s at 200rpm. Reduce rate to 100 or 50 rpm for 120s and then settle for 5 min before sampling.
NOTE:
2490 is CLAR 2537A
1580 is CLAR17650

## May 2022 -Phase G
PHASE G JAR TESTING
Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
1 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 238 | 5 | 249 | 73.7 | 175.3 | there was a nice increase in floc size with increasing floc. Lots of FW in all jars. There was a steady increase in settling rates
| 2 | 8181 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:8181 | 249 | 6
| 3 | 8181 | 1.5 | 2537A | 25 | 25 ppm:2537A 1.5 ppm:8181 | 165 | 4
| 4 | 8181 | 1.75 | 2537A | 25 | 25 ppm:2537A 1.75 ppm:8181 | 133 | 3
| 5 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 113 | 2
| 6 | 8181 | 3 | 2537A | 25 | 25 ppm:2537A 3 ppm:8181 | 73.7 | 1
2 | 1 | blank |  |  |  | ppm: ppm:blank | 307 | 6 | 307 | 48.7 | 258.3 | j2, 2 & 4 showed decent floc size with J4 having the largest. J6 was very fine and J5 was small. During the slow stir there was FW in J3,4&5. settling rates in this order J4>J3>J2>J5>J6.
| 2 | 8181 | 1 | 2537A | 0 | 0 ppm:2537A 1 ppm:8181 | 236 | 5
| 3 | 8181 | 2 | 2537A | 0 | 0 ppm:2537A 2 ppm:8181 | 186 | 3
| 4 | 7767 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7767 | 48.7 | 1
| 5 | 7878 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7878 | 84.2 | 2
| 6 | 7757 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7757 | 191 | 4
3 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 355 | 6 | 355 | 206 | 149 | better particle size than with 7757 and some FW in all jars. Slow settling rate…J4>J5>J6>J3>J2>J1
| 2 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 247 | 3
| 3 | 8181 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:8181 | 206 | 1
| 4 | 8181 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:8181 | 259 | 5
| 5 | 8181 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:8181 | 258 | 4
| 6 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 235 | 2
4 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 346 | 6 | 346 | 69.4 | 276.6 | lots of FW in all Jar with good particle size. Settling rates all very comparable. Lots of very fine particles in all jars.
| 2 | 7767 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7767 | 133 | 5
| 3 | 7767 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 | 76.7 | 2
| 4 | 7767 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7767 | 69.4 | 1
| 5 | 7767 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:7767 | 92.5 | 3
| 6 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 112 | 4
5 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 281 | 6 | 281 | 67.8 | 213.2 | very poor floc size and poor settling rates. J5 was the fastest.
| 2 | 7757 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7757 | 232 | 5
| 3 | 7757 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7757 | 166 | 2
| 4 | 7757 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7757 | 224 | 4
| 5 | 7757 | 1 | 8105:2537A | 20 | 20 ppm:8105:2537A 1 ppm:7757 | 67.8 | 1
| 6 | 7757 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7757 | 185 | 3

## PHASE G - Exp 1 & 2
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | ppm:blank ppm:blank | 238
2 | 8181 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:8181 | 249
3 | 8181 | 1.5 | 2537A | 25 | 25 ppm:2537A 1.5 ppm:8181 | 165
4 | 8181 | 1.75 | 2537A | 25 | 25 ppm:2537A 1.75 ppm:8181 | 133
5 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 113
6 | 8181 | 3 | 2537A | 25 | 25 ppm:2537A 3 ppm:8181 | 73.7
1 | blank |  |  |  | ppm: ppm:blank | 307
2 | 8181 | 1 | 2537A | 0 | 0 ppm:2537A 1 ppm:8181 | 236
3 | 8181 | 2 | 2537A | 0 | 0 ppm:2537A 2 ppm:8181 | 186
4 | 7767 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7767 | 48.7
5 | 7878 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7878 | 84.2
6 | 7757 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7757 | 191
Exp 2 - Floc screen w/ 2537A dosage profile
Exp 1 - 8181 profile w/ 2537A profileblank blank ppm:blank ppm:blank 286 61610 2 2537A 10 10 ppm:2537A 2 ppm:61610 78.2 61610 2 2537A 20 20 ppm:2537A 2 ppm:61610 51.7 61610 2 2537A 30 30 ppm:2537A 2 ppm:61610 36.9 61610 2 2537A 40 40 ppm:2537A 2 ppm:61610 34.3 61610 2 2537A 50 50 ppm:2537A 2 ppm:61610 41.2

## PHASE G - Floc & coag Screen
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank |  | blank |  | ppm:blank ppm:blank | 355
2 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 247
3 | 8181 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:8181 | 206
4 | 8181 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:8181 | 259
5 | 8181 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:8181 | 258
6 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 235
1 | blank |  | blank |  | ppm:blank ppm:blank | 346
2 | 7767 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7767 | 133
3 | 7767 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 | 76.7
4 | 7767 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7767 | 69.4
5 | 7767 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:7767 | 92.5
6 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 112
1 | blank |  | blank |  | ppm:blank ppm:blank | 281
2 | 7757 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7757 | 232
3 | 7757 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7757 | 166
4 | 7757 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7757 | 224
5 | 7757 | 1 | 8105:2537A | 20 | 20 ppm:8105:2537A 1 ppm:7757 | 67.8
6 | 7757 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7757 | 185
Reset Set-Jar Order