## Blend Ratio
Plant Baseline | Rate |  | % composition | Normalized to 1000 mL | x7 | normalize 700 ml
WLS Streams |  | outlet | 947
De-oiled Water | 820 |  | 86.5892 | 865.8923 | 6061.246 | 606.1246
HLS Sludge | 75 |  | 7.9197 | 79.1975 | 554.3823 | 55.4382
Low Pressure BD | 0 |  | 0 | 0 | 0 | 0
Make up Water | 20 |  | 2.1119 | 21.1193 | 147.8353 | 14.7835
Lime | 16 |  | 1.6895 | 16.8955 | 118.2682 | 11.8268
Mag | 16 |  | 1.6895 | 16.8955 | 118.2682 | 11.8268
| 947 |  | 100 | 1000 | 7000 | 700
| 1% | 0.1%
ppm | 10000 | 1000
1 mL in 1L | 10 | 1
1 mL in .7 L | 14.2857 | 1.4286
required dosage (ppm) | 80 | 8
# mL in 1L | 8 | 8
# mL in 0.7 L | 5.6 | 5.6
required dosage (ppm) | # mL in 1L | # mL in 0.7 L |  | required dosage (ppm) | # mL in 1L | # mL in 0.7 L
10 | 1 | 0.69979 |  | 1 | 1 | 0.69979
20 | 2 | 1.3996 |  | 2 | 2 | 1.3996
30 | 3 | 2.0994 |  | 3 | 3 | 2.0994
40 | 4 | 2.7992 |  | 4 | 4 | 2.7992
50 | 5 | 3.499 |  | 5 | 5 | 3.499
60 | 6 | 4.1987 |  | 6 | 6 | 4.1987
70 | 7 | 4.8985 |  | 7 | 7 | 4.8985
80 | 8 | 5.5983 |  | 8 | 8 | 5.5983
90 | 9 | 6.2981 |  | 9 | 9 | 6.2981
100 | 10 | 6.9979 |  | 10 | 10 | 6.9979
110 | 11 | 7.6977 |  | 11 | 11 | 7.6977
120 | 12 | 8.3975 |  | 12 | 12 | 8.3975
130 | 13 | 9.0973
140 | 14 | 9.7971
150 | 15 | 10.4969

## Procedure
Composite Procedure: prepare composite sample with produced water, sludge, MgO & lime all mixed together. Fill jars and add coag while stirring at 200 rpm for 60s, add floc & let stir for 30s, reduce to 100 rpm for 2 mins, then let settle for 5 mins before collecting samples.
Composite minus sludge Procedure:
Slurry Procedure:
NOTE:
2490 is CLAR 2537A
1580 is CLAR17650

## Settling Data Input
Comment | Tap | total Vol | Settling heights (1000 mL Grad cylinder)
|  |  | 30 | 60 | 90 | 120 (2 min) | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) | 5:30 (min) | 360 (6 min) | 6:30 (min) | 420 (7 min) | 7:30 (min) | 480 (8 min) | 8:30 (min) | 540 (9 min) | 9:30 (min) | 600 (10 min) | 10:30 (min) | 11:00 (min)
|  |  |  | 30 | 60 | 90 | 120 | 150 | 180 | 210 | 240 | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)
[5 empty] | 30 | 60 | 90 | 120 | 150 | 180 (3 min) | 210 | 240 (4 min) | 270 | 300 (5 min) |  | 360 (6 min) |  | 420 (7 min) |  | 480 (8 min) |  | 540 (9 min) |  | 600 (10 min)

## Results - Summer 2021
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
2021-08-17 | Composite | 1 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 107 | 6 | 107 | 9.39 | 97.61 | there is a particle size incease with 2495 vs all of the other jars. Also settles fastest with best water clarity
|  |  | 2 | blank |  | 1252 | 10 | 10 ppm:1252 ppm:blank | 76 | 4
|  |  | 3 | blank |  | 2537 | 10 | 10 ppm:2537 ppm:blank | 67.5 | 2
|  |  | 4 | blank |  | 2495 | 10 | 10 ppm:2495 ppm:blank | 9.39 | 1
|  |  | 5 | blank |  | 17650 | 10 | 10 ppm:17650 ppm:blank | 71.5 | 3
|  |  | 6 | blank |  | 8190 | 10 | 10 ppm:8190 ppm:blank | 96.6 | 5
2021-08-17 |  | 2 | 1 | blank |  | blank |  | ppm:blank ppm:blank | 133 | 6 | 133 | 11.7 | 121.3 | particle size increase with floc increase, fw during stir period in j5&6. very similar behaviour from Oct testing. This is a good product combo in terms of water quality
|  |  | 2 | 2531 | 0.2 | 1252 | 10 | 10 ppm:1252 0.2 ppm:2531 | 79 | 5
|  |  | 3 | 2531 | 0.4 | 1252 | 10 | 10 ppm:1252 0.4 ppm:2531 | 51.8 | 4
|  |  | 4 | 2531 | 0.6 | 1252 | 10 | 10 ppm:1252 0.6 ppm:2531 | 29.9 | 3
|  |  | 5 | 2531 | 0.8 | 1252 | 10 | 10 ppm:1252 0.8 ppm:2531 | 21.8 | 2
|  |  | 6 | 2531 | 1 | 1252 | 10 | 10 ppm:1252 1 ppm:2531 | 11.7 | 1
2021-08-18 |  | 3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 91 | 6 | 91 | 6.22 | 84.78
|  |  | 2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 43.2 | 3
|  |  | 3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 27.1 | 2
|  |  | 4 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 6.22 | 1
|  |  | 5 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 54 | 4
|  |  | 6 | 7878 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7878 | 59.6 | 5
2021-08-18 |  | 4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 98.9 | 6 | 98.9 | 4.78 | 94.12 | 7767 shows much better floc formation than 7878 in al jars. Can see FW in both fast and slow stir. 17650 appears to settle fastest but water quality is not as good as 2537 or 2495.
|  |  | 2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 25.7 | 3
|  |  | 3 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 7.92 | 2
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.78 | 1
|  |  | 5 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.2 | 4
|  |  | 6 | 7767 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7767 | 34.8 | 5
2021-08-18 |  | 5 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 91.5 | 6 | 91.5 | 10.4 | 81.1 | J4 & J6 shows large particle size and lots of FW during stirring. J6>J4>JJ2>J1>J5>J3 in terms of settling rate. J6 is showing best water quality
|  |  | 2 | 2531 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:2531 | 14.2 | 2
|  |  | 3 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 55.2 | 4
|  |  | 4 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.6 | 3
|  |  | 5 | 7757 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7757 | 57.3 | 5
|  |  | 6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 10.4 | 1
2021-08-18 |  | 6 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 89.3 | 6 | 89.3 | 3.65 | 85.65 | similar trend as exp 5 with J6 & J4 showing best response. All excellent results wwith 2495, this is same as previous jar testing where 2495 made everything look great. However, 8181 does rank the best.
|  |  | 2 | 2531 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:2531 | 4.2 | 2
|  |  | 3 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 5.39 | 5
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.67 | 3
|  |  | 5 | 7757 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7757 | 4.93 | 4
|  |  | 6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 3.65 | 1
2021-08-18 |  | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 66.2 | 6 | 66.2 | 6.4 | 59.8 | same trend as above. Really liking the response with 8181. J6 & J4 fastesst settling. J 3 & J5 are the slowest, this is interesting since the blank actually settles faster than jars with 7878 or 7757 present.
|  |  | 2 | 2531 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:2531 | 11.4 | 3
|  |  | 3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 25.4 | 5
|  |  | 4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 6.4 | 1
|  |  | 5 | 7757 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7757 | 19 | 4
|  |  | 6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 8.28 | 2
2021-08-18 |  | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 52.4 | 6 | 52.4 | 15.2 | 37.2 | these jars all look good.
|  |  | 2 | 7767 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:7767 | 36 | 5
|  |  | 3 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 24.5 | 4
|  |  | 4 | 7767 | 0.5 | 17650 | 15 | 15 ppm:17650 0.5 ppm:7767 | 21.8 | 3
|  |  | 5 | 8181 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:8181 | 16.6 | 2
|  |  | 6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 15.2 | 1
2021-08-18 |  | 9 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 94.9 | 6 | 94.9 | 4.36 | 90.54 | all fast settling, excellent water quality. Collected at 2 min mark
|  |  | 2 | 7767 | 0.5 | 2495 | 2.5 | 2.5 ppm:2495 0.5 ppm:7767 | 20.2 | 5
|  |  | 3 | 7767 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:7767 | 10.7 | 4
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 5.48 | 2
|  |  | 5 | 8181 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:8181 | 9.03 | 3
|  |  | 6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 4.36 | 1
2021-08-19 |  | 10 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 162 | 6 | 162 | 4.99 | 157.01 | same trends as above. 8181 does an excellent job at particle size. Colleccted turbs at 2 min settling.
|  |  | 2 | 7767 | 0.5 | 2537 | 2.5 | 2.5 ppm:2537 0.5 ppm:7767 | 21 | 5
|  |  | 3 | 7767 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:7767 | 11.6 | 2
|  |  | 4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 4.99 | 1
|  |  | 5 | 8181 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:8181 | 18.7 | 4
|  |  | 6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 12.4 | 3
2021-08-19 |  | 11 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 264 | 6 | 264 | 10.7 | 253.3 | excellent dosage profile, nice gradient with increased particle size, settling rate & clarity. Collected turb @ 2mins
|  |  | 2 | 7767 | 0.2 | 2537 | 5 | 5 ppm:2537 0.2 ppm:7767 | 25.8 | 5
|  |  | 3 | 7767 | 0.4 | 2537 | 5 | 5 ppm:2537 0.4 ppm:7767 | 19.6 | 4
|  |  | 4 | 7767 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:7767 | 13.4 | 3
|  |  | 5 | 7767 | 0.8 | 2537 | 5 | 5 ppm:2537 0.8 ppm:7767 | 11.4 | 2
|  |  | 6 | 7767 | 1 | 2537 | 5 | 5 ppm:2537 1 ppm:7767 | 10.7 | 1
2021-08-19 |  | 12 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 105 | 6 | 105 | 7.76 | 97.24 | excellent dosage profile
|  |  | 2 | 7767 | 0.2 | 2495 | 5 | 5 ppm:2495 0.2 ppm:7767 | 25 | 5
|  |  | 3 | 7767 | 0.4 | 2495 | 5 | 5 ppm:2495 0.4 ppm:7767 | 14.2 | 4
|  |  | 4 | 7767 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:7767 | 9.46 | 3
|  |  | 5 | 7767 | 0.8 | 2495 | 5 | 5 ppm:2495 0.8 ppm:7767 | 7.76 | 1
|  |  | 6 | 7767 | 1 | 2495 | 5 | 5 ppm:2495 1 ppm:7767 | 8.7 | 2
2021-08-19 |  | 13 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 161 | 6 | 161 | 23.4 | 137.6 | lots of FW with increasing floc, large particle size. Settling rate very fast with increasing floc. The sludge is so thick the settling rates are likely skewed as a result. 2min turb
|  |  | 2 | 7767 | 0.2 | 17650 | 10 | 10 ppm:17650 0.2 ppm:7767 | 48.9 | 5
|  |  | 3 | 7767 | 0.4 | 17650 | 10 | 10 ppm:17650 0.4 ppm:7767 | 32.5 | 4
|  |  | 4 | 7767 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:7767 | 26.4 | 3
|  |  | 5 | 7767 | 0.8 | 17650 | 10 | 10 ppm:17650 0.8 ppm:7767 | 25.1 | 2
|  |  | 6 | 7767 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:7767 | 23.4 | 1
2021-08-19 |  | 14 | 1 | 8181 | 0.3 | 17650 | 10 | 10 ppm:17650 0.3 ppm:8181 | 58.6 | 6 | 58.6 | 8.27 | 50.33 | marked difference with 2495 vs 2537 & 17650…FW is observed just with coag addition. Then with floc the particle size is definitely larger for 2495. settling rates are all very fast2 min turbs
|  |  | 2 | 8181 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:8181 | 22 | 4
|  |  | 3 | 8181 | 0.3 | 2495 | 5 | 5 ppm:2495 0.3 ppm:8181 | 17.2 | 3
|  |  | 4 | 8181 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:8181 | 8.27 | 1
|  |  | 5 | 8181 | 0.3 | 2537 | 5 | 5 ppm:2537 0.3 ppm:8181 | 34.8 | 5
|  |  | 6 | 8181 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:8181 | 9.03 | 2
2021-08-19 |  | 15 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 218 | 6 | 218 | 10.8 | 207.2 | this was supposed to be exp 12 but screwed up the coag addition so just went with it and removed the floc. This does show the impact of just coag 2495 with nice gradient in performance. Collected at 2min
|  |  | 2 | blank | 0 | 2495 | 2 | 2 ppm:2495 0 ppm:blank | 70.2 | 5
|  |  | 3 | blank | 0 | 2495 | 4 | 4 ppm:2495 0 ppm:blank | 43.9 | 4
|  |  | 4 | blank | 0 | 2495 | 6 | 6 ppm:2495 0 ppm:blank | 28.4 | 3
|  |  | 5 | blank | 0 | 2495 | 8 | 8 ppm:2495 0 ppm:blank | 14.9 | 2
|  |  | 6 | blank | 0 | 2495 | 10 | 10 ppm:2495 0 ppm:blank | 10.8 | 1

## Trial test - Sept 2021
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
2021-09-23 | 200 rpm fast, then 100 slow | 1 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 262 | 6 | 262 | 85.3 | 176.7 | definitely poorer water calirty at this rate. Let settle for 5 mins
|  |  | 2 | 7767 | 0.5 | 2490 | 5 | 5 ppm:2490 0.5 ppm:7767 | 142 | 5
|  |  | 3 | 7767 | 0.5 | 2490 | 10 | 10 ppm:2490 0.5 ppm:7767 | 85.3 | 1
|  |  | 4 | 7767 | 0.5 | 2490 | 15 | 15 ppm:2490 0.5 ppm:7767 | 119 | 4
|  |  | 5 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 94.8 | 2
|  |  | 6 | 7767 | 0.5 | 2490 | 25 | 25 ppm:2490 0.5 ppm:7767 | 102 | 3
2021-09-23 | same as 1 | 2 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 354 | 6 | 354 | 15.2 | 338.8 | good dosage response, increase water clarity with floc increase
|  |  | 2 | 7767 | 0.5 | 2490 | 10 | 10 ppm:2490 0.5 ppm:7767 | 84.7 | 5
|  |  | 3 | 7767 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 | 52.1 | 4
|  |  | 4 | 7767 | 1.5 | 2490 | 10 | 10 ppm:2490 1.5 ppm:7767 | 33.7 | 3
|  |  | 5 | 7767 | 2 | 2490 | 10 | 10 ppm:2490 2 ppm:7767 | 20.6 | 2
|  |  | 6 | 7767 | 2.5 | 2490 | 10 | 10 ppm:2490 2.5 ppm:7767 | 15.2 | 1
2021-09-23 | same as 1 | 3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 388 | 6 | 388 | 44.7 | 343.3 | j2-4 settle very quick and good clarity, J5 was terrible and J6 did settle decent but clarity not great
|  |  | 2 | 7767 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 | 46 | 2
|  |  | 3 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 49.6 | 3
|  |  | 4 | 7767 - plant | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 - plant | 44.7 | 1
|  |  | 5 | 7878 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7878 | 294 | 5
|  |  | 6 | 8181 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:8181 | 188 | 4
2021-09-24 | same as 1 | 4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 322 | 6 |  |  |  | 8105 looked really good
|  |  | 2 | 7767 - p | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 - p | 32.3 | 4
|  |  | 3 | 7767 - p | 1 | 2490 | 20 | 20 ppm:2490 1 ppm:7767 - p | 44.7 | 5
|  |  | 4 | 7767 - p | 1 | 2490 | 30 | 30 ppm:2490 1 ppm:7767 - p | 23.3 | 3
|  |  | 5 | 7767 - p | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 - p | 20.9 | 2
|  |  | 6 | 7767 - p | 1 | 8105 | 40 | 40 ppm:8105 1 ppm:7767 - p | 6.86 | 1
2021-09-24 |  | 6 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 267 | 6 |  |  |  | really good respoonse with increasing coag
|  |  | 2 | 7767 - p | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7767 - p | 48.6 | 5
|  |  | 3 | 7767 - p | 1 | 2537 | 20 | 20 ppm:2537 1 ppm:7767 - p | 40.2 | 4
|  |  | 4 | 7767 - p | 1 | 2537 | 30 | 30 ppm:2537 1 ppm:7767 - p | 18.5 | 2
|  |  | 5 | 7767 - p | 1 | 2537 | 40 | 40 ppm:2537 1 ppm:7767 - p | 21.6 | 3
|  |  | 6 | 7767 - p | 1 | 2537 | 50 | 50 ppm:2537 1 ppm:7767 - p | 13.2 | 1
2021-09-24 |  | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 299 | 6
|  |  | 2 | 7767 - p | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7767 - p | 77.8 | 5
|  |  | 3 | 7767 - p | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 - p | 49.7 | 3
|  |  | 4 | 7767 - p | 1 | 8105 | 30 | 30 ppm:8105 1 ppm:7767 - p | 17.2 | 1
|  |  | 5 | 7767 - p | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 - p | 54.2 | 4
|  |  | 6 | 7767 - p | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:7767 - p | 44.1 | 2
2021-09-30 |  | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 289 | 6 |  |  |  | J5 & J6 visually looks better during the low stir period…seems to generate bigger flocs.
|  |  | 2 | 7767 - p | 1 | 2537 | 5 | 5 ppm:2537 1 ppm:7767 - p | 36.1 | 3
|  |  | 3 | 7767 - p | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7767 - p | 30.1 | 2
|  |  | 4 | 7767 - p | 1 | 2537 | 15 | 15 ppm:2537 1 ppm:7767 - p | 27 | 1
|  |  | 5 | 7767 - p | 1 | NCC-CL | 5 | 5 ppm:NCC-CL 1 ppm:7767 - p | 47.8 | 5
|  |  | 6 | 7767 - p | 1 | NCC-CL | 10 | 10 ppm:NCC-CL 1 ppm:7767 - p | 36.8 | 4
9
10
2021-09-23 | 200 rpm fast, then 100 slow | 16 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 262 | 6 | 262 | 85.3 | 176.7 | definitely poorer water calirty at this rate. Let settle for 5 mins
|  |  | 2 | 7767 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:7767 | 142 | 5
|  |  | 3 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 85.3 | 1
|  |  | 4 | 7767 | 0.5 | 2537 | 15 | 15 ppm:2537 0.5 ppm:7767 | 119 | 4
|  |  | 5 | 7767 | 0.5 | 2537 | 20 | 20 ppm:2537 0.5 ppm:7767 | 94.8 | 2
|  |  | 6 | 7767 | 0.5 | 2537 | 25 | 25 ppm:2537 0.5 ppm:7767 | 102 | 3
2021-09-23 | same as 16 | 17 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 354 | 6 | 354 | 15.2 | 338.8 | good dosage response, increase water clarity with floc increase
|  |  | 2 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 84.7 | 5
|  |  | 3 | 7767 | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7767 | 52.1 | 4
|  |  | 4 | 7767 | 1.5 | 2537 | 10 | 10 ppm:2537 1.5 ppm:7767 | 33.7 | 3
|  |  | 5 | 7767 | 2 | 2537 | 10 | 10 ppm:2537 2 ppm:7767 | 20.6 | 2
|  |  | 6 | 7767 | 2.5 | 2537 | 10 | 10 ppm:2537 2.5 ppm:7767 | 15.2 | 1
2021-09-23 | same as 16 | 18 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 388 | 6 | 388 | 44.7 | 343.3 | j2-4 settle very quick and good clarity, J5 was terrible and J6 did settle decent but clarity not great
|  |  | 2 | 7767 | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7767 | 46 | 2
|  |  | 3 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 49.6 | 3
|  |  | 4 | 7767 - plant | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7767 - plant | 44.7 | 1
|  |  | 5 | 7878 | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:7878 | 294 | 5
|  |  | 6 | 8181 | 1 | 2537 | 10 | 10 ppm:2537 1 ppm:8181 | 188 | 4
|  | 19 | 1 |  |  |  |  | ppm: ppm: |  | #N/A | 0 | 0 | 0
|  |  | 2 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 3 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 4 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 5 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 6 |  |  |  |  | ppm: ppm: |  | #N/A
|  |  | 1 |  |  |  |  | ppm: ppm:
|  |  | 2 |  |  |  |  | ppm: ppm:
|  |  | 3 |  |  |  |  | ppm: ppm:
|  |  | 4 |  |  |  |  | ppm: ppm:
|  |  | 5 |  |  |  |  | ppm: ppm:
|  |  | 6 |  |  |  |  | ppm: ppm:

## Floc Baseline Plot
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank |  | blank |  | blank | 133
2 | 2531 | 0.2 | 1252 | 10 | 10 ppm:1252 0.2 ppm:2531 | 79
3 | 2531 | 0.4 | 1252 | 10 | 10 ppm:1252 0.4 ppm:2531 | 51.8
4 | 2531 | 0.6 | 1252 | 10 | 10 ppm:1252 0.6 ppm:2531 | 29.9
5 | 2531 | 0.8 | 1252 | 10 | 10 ppm:1252 0.8 ppm:2531 | 21.8
6 | 2531 | 1 | 1252 | 10 | 10 ppm:1252 1 ppm:2531 | 11.7
1 | blank | 0 | blank | 0 | blank | 197
2 | 2531 | 0.2 | 1252 | 10 | 10 ppm:1252 0.2 ppm:2531 | 72.6
3 | 2531 | 0.4 | 1252 | 10 | 10 ppm:1252 0.4 ppm:2531 | 26.5
4 | 2531 | 0.6 | 1252 | 10 | 10 ppm:1252 0.6 ppm:2531 | 23.8
5 | 2531 | 0.8 | 1252 | 10 | 10 ppm:1252 0.8 ppm:2531 | 20.6
6 | 2531 | 1 | 1252 | 10 | 10 ppm:1252 1 ppm:2531 | 7.04

## Floc screen - Aug 2021
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank | 0 | blank | 0 | blank | 91.5
2 | 2531 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:2531 | 14.2
3 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 55.2
4 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.6
5 | 7757 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7757 | 57.3
6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 10.4
1 | blank | 0 | blank | 0 | blank | 89.3
2 | 2531 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:2531 | 4.2
3 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 5.39
4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.67
5 | 7757 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7757 | 4.93
6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 3.65
1 | blank | 0 | blank | 0 | blank | 66.2
2 | 2531 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:2531 | 11.4
3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 25.4
4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 6.4
5 | 7757 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7757 | 19
6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 8.28
Reset Set-Jar Order

## Floc screen - Oct 2020
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank | 0 | blank | 0 | blank | 113
2 | 7768 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7768 | 51.9
3 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 39.4
4 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 23.9
5 | 7763 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7763 | 53
6 | 61610 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:61610 | 84.8
1 | blank | 0 | blank | 0 | blank | 174
2 | 7768 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7768 | 7.11
3 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 5.84
4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 9.6
5 | 7763 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7763 | 5.83
6 | 61610 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:61610 | 7.09
1 | blank | 0 | blank |  | blank | 66.1
2 | 7768 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7768 | 24.5
3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 41.9
4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 8.72
5 | 7763 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7763 | 56.2
6 | 61610 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:61610 | 64.5
Reset Set-Jar Order

## 7767 dosage profile -Aug 2020
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank | 0 | blank | 0 | blank | 161
2 | 7767 | 0.2 | 17650 | 10 | 10 ppm:17650 0.2 ppm:7767 | 48.9
3 | 7767 | 0.4 | 17650 | 10 | 10 ppm:17650 0.4 ppm:7767 | 32.5
4 | 7767 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:7767 | 26.4
5 | 7767 | 0.8 | 17650 | 10 | 10 ppm:17650 0.8 ppm:7767 | 25.1
6 | 7767 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:7767 | 23.4
1 | blank | 0 | blank | 0 | blank | 105
2 | 7767 | 0.2 | 2495 | 5 | 5 ppm:2495 0.2 ppm:7767 | 25
3 | 7767 | 0.4 | 2495 | 5 | 5 ppm:2495 0.4 ppm:7767 | 14.2
4 | 7767 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:7767 | 9.46
5 | 7767 | 0.8 | 2495 | 5 | 5 ppm:2495 0.8 ppm:7767 | 7.76
6 | 7767 | 1 | 2495 | 5 | 5 ppm:2495 1 ppm:7767 | 8.7
1 | blank | 0 | blank | 0 | blank | 264
2 | 7767 | 0.2 | 2537 | 5 | 5 ppm:2537 0.2 ppm:7767 | 25.8
3 | 7767 | 0.4 | 2537 | 5 | 5 ppm:2537 0.4 ppm:7767 | 19.6
4 | 7767 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:7767 | 13.4
5 | 7767 | 0.8 | 2537 | 5 | 5 ppm:2537 0.8 ppm:7767 | 11.4
6 | 7767 | 1 | 2537 | 5 | 5 ppm:2537 1 ppm:7767 | 10.7
Reset Set-Jar Order

## 8181 screen
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | 8181 | 0.3 | 17650 | 10 | 10 ppm:17650 0.3 ppm:8181 | 58.6
2 | 8181 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:8181 | 22
3 | 8181 | 0.3 | 2495 | 5 | 5 ppm:2495 0.3 ppm:8181 | 17.2
4 | 8181 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:8181 | 8.27
5 | 8181 | 0.3 | 2537 | 5 | 5 ppm:2537 0.3 ppm:8181 | 34.8
6 | 8181 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:8181 | 9.03
5 | 8181 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:8181 | 16.6
6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 15.2
5 | 8181 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:8181 | 9.03
6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 4.36
5 | 8181 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:8181 | 18.7
6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 12.4
Exp 14
J5&6 from Exp 8-10

## Coag screen
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank |  | blank |  | blank | 107
2 | blank |  | 1252 | 10 | 10 ppm:1252 | 76
3 | blank |  | 2537 | 10 | 10 ppm:2537 | 67.5
4 | blank |  | 2495 | 10 | 10 ppm:2495 | 9.39
5 | blank |  | 17650 | 10 | 10 ppm:17650 | 71.5
6 | blank |  | 8190 | 10 | 10 ppm:8190 | 96.6
1 | blank | 0 | blank | 0 | blank | 91
2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 43.2
3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 27.1
4 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 6.22
5 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 54
6 | 7878 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7878 | 59.6
1 | blank | 0 | blank | 0 | blank | 98.9
2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 25.7
3 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 7.92
4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.78
5 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.2
6 | 7767 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7767 | 34.8
Reset Set-Jar Order

## Coag dosage profile - Aug 2021
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank | 0 | blank | 0 | blank | 52.4
2 | 7767 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:7767 | 36
3 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 24.5
4 | 7767 | 0.5 | 17650 | 15 | 15 ppm:17650 0.5 ppm:7767 | 21.8
5 | 8181 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:8181 | 16.6
6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 15.2
1 | blank | 0 | blank | 0 | blank | 94.9
2 | 7767 | 0.5 | 2495 | 2.5 | 2.5 ppm:2495 0.5 ppm:7767 | 20.2
3 | 7767 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:7767 | 10.7
4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 5.48
5 | 8181 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:8181 | 9.03
6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 4.36
1 | blank | 0 | blank | 0 | blank | 162
2 | 7767 | 0.5 | 2537 | 2.5 | 2.5 ppm:2537 0.5 ppm:7767 | 21
3 | 7767 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:7767 | 11.6
4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 4.99
5 | 8181 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:8181 | 18.7
6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 12.4
Reset Set-Jar Order

## Coag dosage profile - Oct 2020
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | #REF! | 0 | Blank |  | 0
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 305
2 | 7767 | 0.4 | 17650 | 2 | 2 ppm:17650 0.4 ppm:7767 | 125
3 | 7767 | 0.4 | 17650 | 4 | 4 ppm:17650 0.4 ppm:7767 | 102
4 | 7767 | 0.4 | 17650 | 6 | 6 ppm:17650 0.4 ppm:7767 | 64.3
5 | 7767 | 0.4 | 17650 | 8 | 8 ppm:17650 0.4 ppm:7767 | 70.2
6 | 7767 | 0.4 | 17650 | 10 | 10 ppm:17650 0.4 ppm:7767 | 70.8
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 133
2 | 7767 | 0.4 | 2495 | 2 | 2 ppm:2495 0.4 ppm:7767 | 32.2
3 | 7767 | 0.4 | 2495 | 4 | 4 ppm:2495 0.4 ppm:7767 | 20.1
4 | 7767 | 0.4 | 2495 | 6 | 6 ppm:2495 0.4 ppm:7767 | 10.7
5 | 7767 | 0.4 | 2495 | 8 | 8 ppm:2495 0.4 ppm:7767 | 7.41
6 | 7767 | 0.4 | 2495 | 10 | 10 ppm:2495 0.4 ppm:7767 | 4.35
1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 104
2 | 7767 | 0.4 | 2537 | 2 | 2 ppm:2537 0.4 ppm:7767 | 28.6
3 | 7767 | 0.4 | 2537 | 4 | 4 ppm:2537 0.4 ppm:7767 | 13.8
4 | 7767 | 0.4 | 2537 | 6 | 6 ppm:2537 0.4 ppm:7767 | 10.5
5 | 7767 | 0.4 | 2537 | 8 | 8 ppm:2537 0.4 ppm:7767 | 5.86
6 | 7767 | 0.4 | 2537 | 10 | 10 ppm:2537 0.4 ppm:7767 | 4
Reset Set-Jar Order

## 2495 w & wo floc
Jar | Flocculant Used | Floc ppm | Coagulant Used | Coag ppm | Chemicals | NTU
1 | blank | 0 | blank | 0 | blank | 105
2 | 7767 | 0.2 | 2495 | 5 | 5 ppm:2495 0.2 ppm:7767 | 25
3 | 7767 | 0.4 | 2495 | 5 | 5 ppm:2495 0.4 ppm:7767 | 14.2
4 | 7767 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:7767 | 9.46
5 | 7767 | 0.8 | 2495 | 5 | 5 ppm:2495 0.8 ppm:7767 | 7.76
6 | 7767 | 1 | 2495 | 5 | 5 ppm:2495 1 ppm:7767 | 8.7
1 | blank | 0 | blank | 0 | blank | 218
2 | blank | 0 | 2495 | 2 | 2 ppm:2495 | 70.2
3 | blank | 0 | 2495 | 4 | 4 ppm:2495 | 43.9
4 | blank | 0 | 2495 | 6 | 6 ppm:2495 | 28.4
5 | blank | 0 | 2495 | 8 | 8 ppm:2495 | 14.9
6 | blank | 0 | 2495 | 10 | 10 ppm:2495 | 10.8