## Jan 2022
PHASE F JAR TESTING |  |  |  |  | 0 |  | 0
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
1/20/22 | standard | 1 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 99.3 | 899.7 | 7767 settled faster with all coags but 7878 did give a better water quality
|  |  | 2 | 7767 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7767 | 613 | 4
|  |  | 3 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 195 | 2
|  |  | 4 | 7767 | 0.5 | 1580 | 10 | 10 ppm:1580 0.5 ppm:7767 | 700 | 5
|  |  | 5 | 7878 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7878 | 344 | 3
|  |  | 6 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 99.3 | 1
1/20/22 | standard | 2 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 915 | 6 | 915 | 249 | 666 | visually theres little difference, may settle faster with more coag but not significantly
|  |  | 2 | 7767 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:7767 | 662 | 5
|  |  | 3 | 7767 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:7767 | 487 | 4
|  |  | 4 | 7767 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:7767 | 375 | 3
|  |  | 5 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 273 | 2
|  |  | 6 | 7767 | 0.5 | 2537A | 25 | 25 ppm:2537A 0.5 ppm:7767 | 249 | 1
1/20/22 |  | 3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 245 | 754 | big difference with increasing floc, particle size is much bigger with a good gradient and there is increasingly more FW during the stir period. Settling is also increase with more floc. Water clarity still isn't amazing, jars are very hazy.
|  |  | 2 | 7767 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:7767 | 691 | 5
|  |  | 3 | 7767 | 1 | 2537A | 5 | 5 ppm:2537A 1 ppm:7767 | 451 | 4
|  |  | 4 | 7767 | 1.5 | 2537A | 5 | 5 ppm:2537A 1.5 ppm:7767 | 310 | 3
|  |  | 5 | 7767 | 2 | 2537A | 5 | 5 ppm:2537A 2 ppm:7767 | 303 | 2
|  |  | 6 | 7767 | 2.5 | 2537A | 5 | 5 ppm:2537A 2.5 ppm:7767 | 245 | 1
1/20/22 |  | 4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 96.7 | 902.3
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 430 | 5
|  |  | 3 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 242 | 4
|  |  | 4 | 7767 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:7767 | 146 | 3
|  |  | 5 | 7767 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:7767 | 130 | 2
|  |  | 6 | 7767 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:7767 | 96.7 | 1
1/20/22 |  | 5 | 1 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 170 | 2 | 464 | 122 | 342 | 7767 is clearly showing the best particle formation. 7878 shows the worst particle size and settling rate.
|  |  | 2 | 7878 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7878 | 280 | 3
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 122 | 1
|  |  | 4 | 7767 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 | 356 | 4
|  |  | 5 | 7878 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7878 | 464 | 6
|  |  | 6 | 8181 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:8181 | 386 | 5
1/20/22 |  | 6 | 1 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 119 | 5 | 208 | 28.4 | 179.6 | some difference between the coags but all seemed to have very similar performance with particle size & settling
|  |  | 2 | 7767 | 1 | 2490 | 20 | 20 ppm:2490 1 ppm:7767 | 37.7 | 2
|  |  | 3 | 7767 | 1 | 2495 | 20 | 20 ppm:2495 1 ppm:7767 | 28.4 | 1
|  |  | 4 | 7767 | 1 | 8190 | 20 | 20 ppm:8190 1 ppm:7767 | 208 | 6
|  |  | 5 | 7767 | 1 | 8105 | 20 | 20 ppm:8105 1 ppm:7767 | 113 | 4
|  |  | 6 | 7767 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:7767 | 110 | 3
| use phase F sludge | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 42.6 | 956.4 | 7767 still had the best particle size then followed by 8182. J4 visible FW during stir & settled fastest. J4 still looked the best in all aspects
|  |  | 2 | 2531 | 1 | 1252 | 20 | 20 ppm:1252 1 ppm:2531 | 119 | 4
|  |  | 3 | 2531 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:2531 | 42.6 | 1
|  |  | 4 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 52.3 | 2
|  |  | 5 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 59 | 3
|  |  | 6 | 8182 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8182 | 292 | 5
| use phase G sludge | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 400 | 6 | 400 | 5.81 | 394.19 | similar sludge as F. Settling rate J4>J2>J3>J5>J6…very good water quality, sampled after 1 min settling. J4 showed best size and settling rate, lots of FW.
|  |  | 2 | 2531 | 1 | 1252 | 20 | 20 ppm:1252 1 ppm:2531 | 20.1 | 3
|  |  | 3 | 2531 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:2531 | 12.4 | 2
|  |  | 4 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 5.81 | 1
|  |  | 5 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 35.2 | 4
|  |  | 6 | 8182 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8182 | 43.1 | 5
| back to F phase sludge | 9 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 6 | 999 | 7.33 | 991.67 | there was an increase in size just with coag addition and with floc there was still a good gradient. Even during the slow mix there was an increase in FW with the coag increase. Measured turb at 2 min
|  |  | 2 | 7767 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:7767 | 59 | 5
|  |  | 3 | 7767 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7767 | 48 | 4
|  |  | 4 | 7767 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:7767 | 30.6 | 3
|  |  | 5 | 7767 | 1 | 2537A | 40 | 40 ppm:2537A 1 ppm:7767 | 13.6 | 2
|  |  | 6 | 7767 | 1 | 2537A | 50 | 50 ppm:2537A 1 ppm:7767 | 7.33 | 1

## March 2022
PHASE E JAR TESTING |  |  |  |  | 0 | 0 | 0
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
3-23-2022 |  | 1 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 228 | 6 | 228 | 106 | 122 | J6, J5 settled fastest. During stirring J6 lookedd to have more FW. They all look garbage wrt clarity
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 115 | 2
|  |  | 3 | 7767 | 0.5 | 2490 | 20 | 20 ppm:2490 0.5 ppm:7767 | 106 | 1
|  |  | 4 | 7767 | 0.5 | 8190 | 20 | 20 ppm:8190 0.5 ppm:7767 | 137 | 4
|  |  | 5 | 7767 | 0.5 | 1580 | 20 | 20 ppm:1580 0.5 ppm:7767 | 146 | 5
|  |  | 6 | 7767 | 0.5 | 8105 | 20 | 20 ppm:8105 0.5 ppm:7767 | 126 | 3
3-23-2022 |  | 2 | 1 | 2531 | 0.5 | 1252 | 20 | 20 ppm:1252 0.5 ppm:2531 | 375 | 6 | 375 | 47.2 | 327.8 | J2 is the only jar with FW and it has the largest partcile size. J2>j1>J4>j6>5>j3 order of settling rates.
|  |  | 2 | 7767 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7767 | 47.2 | 1
|  |  | 3 | 7878 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7878 | 53.4 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 87.1 | 3
|  |  | 5 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 261 | 5
|  |  | 6 | 7757 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:7757 | 224 | 4
3-24-2022 |  | 3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 304 | 6 | 304 | 108 | 196
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 185 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 162 | 4
|  |  | 4 | 8181 | 0.5 | 2537A | 40 | 40 ppm:2537A 0.5 ppm:8181 | 120 | 2
|  |  | 5 | 8181 | 0.5 | 2537A | 50 | 50 ppm:2537A 0.5 ppm:8181 | 108 | 1
|  |  | 6 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 125 | 3
3-24-2022 |  | 4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 214 | 6 | 214 | 43.5 | 170.5 | the increase floc did give larger particle size and there was more FW with the increase. Also the settling rate was linear with the increase. Water clarity is all over the place…need to repeat this experiment
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 105 | 2
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 168 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 43.5 | 1
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 143 | 3
3-24-2022 |  | 5 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 227 | 6 | 227 | 91.8 | 135.2 | repeat exp 4. same observations. 21s<25<28<32<48 is the settling times to get a defined slduge edge in jars ordered 6-1. J 6 settled fastest.
|  |  | 2 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 171 | 3
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 92.2 | 2
|  |  | 4 | 8181 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:8181 | 179 | 5
|  |  | 5 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 172 | 4
|  |  | 6 | 8181 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:8181 | 91.8 | 1
3-24-2022 |  | 6 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 213 | 6 | 213 | 24.3 | 188.7 | significaant improvement in the amount of FW at 5 ppm 8181. 17s< 21s was the settling times for J6 & J5. interestingly yhe settling times for J2< J3<J4 is in this order…less coag it settles faster???
|  |  | 2 | 8181 | 0.5 | 2537A | 5 | 5 ppm:2537A 0.5 ppm:8181 | 181 | 5
|  |  | 3 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 151 | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 166 | 4
|  |  | 5 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 159 | 3
|  |  | 6 | 8181 | 5 | 2537A | 10 | 10 ppm:2537A 5 ppm:8181 | 24.3 | 1
3-24-2022 |  | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 210 | 6 | 210 | 36.5 | 173.5 | particle size increase with more floc & increase FW. J 6 w/o coag probably as the same amount of FW as J5 with coag. Seems like the coag is preventing improvement. J5 did settle faste than J6 but J6 was same rate as J4. The increase in floc did give faster settling. also visual improvement in water clarity
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 194 | 5
|  |  | 3 | 8181 | 4 | 2537A | 10 | 10 ppm:2537A 4 ppm:8181 | 159 | 4
|  |  | 4 | 8181 | 6 | 2537A | 10 | 10 ppm:2537A 6 ppm:8181 | 44.4 | 2
|  |  | 5 | 8181 | 8 | 2537A | 10 | 10 ppm:2537A 8 ppm:8181 | 36.5 | 1
|  |  | 6 | 8181 | 4 | 2537A | 0 | 0 ppm:2537A 4 ppm:8181 | 94.6 | 3
3-25-2022 |  | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 221 | 6 | 221 | 45 | 176 | no obvious difference in size with increase in coag or amount of FW. Reverse trend with settling rate…its slower as coag increases. FLOC controls bed & particle size.
|  |  | 2 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 174 | 5
|  |  | 3 | 8181 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:8181 | 147 | 3
|  |  | 4 | 8181 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:8181 | 148 | 4
|  |  | 5 | 8181 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:8181 | 126 | 2
|  |  | 6 | 8181 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:8181 | 45 | 1
3-25-2023 |  | 9 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 196 | 4 | 321 | 127 | 194 | J4&J5 does look slightly better than the other jars during the stir period. J5>J6>J1>J3>j2 IN ORDER OF FASTEST SETTLING RATES. Note- MgO collected from phase G since it was plugged in phase E. Phase G uses PW in the slurry whereas Phase E uses soften brackish
|  |  | 2 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 179 | 2
|  |  | 3 | 8181 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:8181 | 127 | 1
|  |  | 4 | 8181 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:8181 | 321 | 6
|  |  | 5 | 8181 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:8181 | 194 | 3
|  |  | 6 | 8181 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:8181 | 261 | 5
3-25-2024 |  | 10 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 295 | 6 | 295 | 24.5 | 270.5 | same MgO issue as Exp 9. really nice trend in size & FW with the increase…visible sludge line at 21 s for J6 & J5, ~ 23s for J4, 26s for J3 & 35s for J2. So good settling response with more floc.
|  |  | 2 | 61610 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:61610 | 161 | 5
|  |  | 3 | 61610 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:61610 | 98.7 | 4
|  |  | 4 | 61610 | 1.5 | 2537A | 20 | 20 ppm:2537A 1.5 ppm:61610 | 89.2 | 3
|  |  | 5 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 24.5 | 1
|  |  | 6 | 61610 | 2.5 | 2537A | 20 | 20 ppm:2537A 2.5 ppm:61610 | 28.1 | 2
3-25-2025 |  | 12 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 286 | 6 | 286 | 34.3 | 251.7 | no change in size, but the FW was higher in J1 vs J6, in that order. settling rates were all comparable.
|  |  | 2 | 61610 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:61610 | 78.2 | 5
|  |  | 3 | 61610 | 2 | 2537A | 20 | 20 ppm:2537A 2 ppm:61610 | 51.7 | 4
|  |  | 4 | 61610 | 2 | 2537A | 30 | 30 ppm:2537A 2 ppm:61610 | 36.9 | 2
|  |  | 5 | 61610 | 2 | 2537A | 40 | 40 ppm:2537A 2 ppm:61610 | 34.3 | 1
|  |  | 6 | 61610 | 2 | 2537A | 50 | 50 ppm:2537A 2 ppm:61610 | 41.2 | 3
3-25-2026 |  | 13 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank |  | #N/A | 0 | 0 | 0
|  |  | 2 | 61610 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:61610 |  | #N/A
|  |  | 3 | 61610 | 2 | 2490 | 25 | 25 ppm:2490 2 ppm:61610 |  | #N/A
|  |  | 4 | 61610 | 2 | 8190 | 25 | 25 ppm:8190 2 ppm:61610 |  | #N/A
|  |  | 5 | 61610 | 2 | 1580 | 25 | 25 ppm:1580 2 ppm:61610 |  | #N/A
|  |  | 6 | 61610 | 2 | 8105 | 25 | 25 ppm:8105 2 ppm:61610 |  | #N/A
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0
[5 empty] | 0 | 0 | 0

## May 2022 Phase G
PHASE G JAR TESTING |  |  |  |  | 0
Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
1 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 238 | 5 | 249 | 73.7 | 175.3 | there was a nice increase in floc size with increasing floc. Lots of FW in all jars. There was a steady increase in settling rates
| 2 | 8181 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:8181 | 249 | 6
| 3 | 8181 | 1.5 | 2537A | 25 | 25 ppm:2537A 1.5 ppm:8181 | 165 | 4
| 4 | 8181 | 1.75 | 2537A | 25 | 25 ppm:2537A 1.75 ppm:8181 | 133 | 3
| 5 | 8181 | 2 | 2537A | 25 | 25 ppm:2537A 2 ppm:8181 | 113 | 2
| 6 | 8181 | 3 | 2537A | 25 | 25 ppm:2537A 3 ppm:8181 | 73.7 | 1
2 | 1 | blank | 0 |  | 0 | 0 ppm: 0 ppm:blank | 307 | 6 | 307 | 48.7 | 258.3 | j2, 2 & 4 showed decent floc size with J4 having the largest. J6 was very fine and J5 was small. During the slow stir there was FW in J3,4&5. settling rates in this order J4>J3>J2>J5>J6.
| 2 | 8181 | 1 | 2537A | 0 | 0 ppm:2537A 1 ppm:8181 | 236 | 5
| 3 | 8181 | 2 | 2537A | 0 | 0 ppm:2537A 2 ppm:8181 | 186 | 3
| 4 | 7767 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7767 | 48.7 | 1
| 5 | 7878 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7878 | 84.2 | 2
| 6 | 7757 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:7757 | 191 | 4
3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 355 | 6 | 355 | 206 | 149 | better particle size than with 7757 and some FW in all jars. Slow settling rate…J4>J5>J6>J3>J2>J1
| 2 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 247 | 3
| 3 | 8181 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:8181 | 206 | 1
| 4 | 8181 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:8181 | 259 | 5
| 5 | 8181 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:8181 | 258 | 4
| 6 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 235 | 2
4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 346 | 6 | 346 | 69.4 | 276.6 | lots of FW in all Jar with good particle size. Settling rates all very comparable. Lots of very fine particles in all jars.
| 2 | 7767 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7767 | 133 | 5
| 3 | 7767 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7767 | 76.7 | 2
| 4 | 7767 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7767 | 69.4 | 1
| 5 | 7767 | 1 | 8105:2537A | 10 | 10 ppm:8105:2537A 1 ppm:7767 | 92.5 | 3
| 6 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 112 | 4
5 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 281 | 6 | 281 | 67.8 | 213.2 | very poor floc size and poor settling rates. J5 was the fastest.
| 2 | 7757 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:7757 | 232 | 5
| 3 | 7757 | 1 | 2490 | 10 | 10 ppm:2490 1 ppm:7757 | 166 | 2
| 4 | 7757 | 1 | 8105 | 10 | 10 ppm:8105 1 ppm:7757 | 224 | 4
| 5 | 7757 | 1 | 8105:2537A | 20 | 20 ppm:8105:2537A 1 ppm:7757 | 67.8 | 1
| 6 | 7757 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7757 | 185 | 3

## July 2022
PHASE F JAR TESTING
Date | Test | procedure | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | Trub % decrease | RANK | MAX | MIN | RANGE | Comment
2022-07-19 | 1 | standard 200 rpm & 100 rpm, 5 min settling | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 651 | 0% | 6 | 651 | 260 | 391 | J3 larger particle during stir & more FW. Settling rates are all very similar. Let settle for 5 mins. The water clarity in J3 was terrible.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 260 | 60.06% | 1
|  |  | 3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 549 | 15.67% | 4
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 557 | 14.44% | 5
|  |  | 5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 408 | 37.33% | 3
|  |  | 6 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 290 | 55.45% | 2
2022-07-19 | 2 | standard 200 rpm & 100 rpm, 5 min settling | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 847 | 0% | 6 | 847 | 96.7 | 750.3 | J6 looks the best with high clarity and lots of FW during stir. All jars have same particle size. J 6 settled the fastest and the other jars were about the same.
|  |  | 2 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 310 | 63.4% | 5
|  |  | 3 | 8181 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:8181 | 186 | 78.04% | 3
|  |  | 4 | 8181 | 1 | 1580 | 25 | 25 ppm:1580 1 ppm:8181 | 96.7 | 88.58% | 1
|  |  | 5 | 8181 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:8181 | 121 | 85.71% | 2
|  |  | 6 | 3058 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:3058 | 206 | 75.68% | 4
2022-07-20 | 3 | slurry method - 200 & 100 rpm | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 765 | 0% | 6 | 765 | 108 | 657 | No partciles with coag addition. J3 shows best flocs and it settles faster but the water clarity is not great. The other jars all settled about the same rate.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 246 | 67.84% | 4
|  |  | 3 | 3058 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:3058 | 290 | 62.09% | 5
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 197 | 74.25% | 2
|  |  | 5 | 8181 | 1 | 8190 | 15 | 15 ppm:8190 1 ppm:8181 | 243 | 68.24% | 3
|  |  | 6 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 108 | 85.88% | 1
2022-07-20 | 4 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 776 | 0% | 6 | 776 | 97.6 | 678.4 | all jars with coag didn't give any initial particle formation. The addition of floc showed good growth and J6 had the best size. Lots of FW during the stir period for J6. J6 showed fastest settling rate. Next J2 through J5 so the increase in coag actually decreased the settling rate with 1580.
|  |  | 2 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 260 | 66.49% | 5
|  |  | 3 | 8181 | 1 | 1580 | 20 | 20 ppm:1580 1 ppm:8181 | 163 | 78.99% | 4
|  |  | 4 | 8181 | 1 | 1580 | 25 | 25 ppm:1580 1 ppm:8181 | 143 | 81.57% | 3
|  |  | 5 | 8181 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:8181 | 97.6 | 87.42% | 1
|  |  | 6 | 3058 | 1 | 1580 | 30 | 30 ppm:1580 1 ppm:3058 | 127 | 83.63% | 2
2022-07-20 | 5 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 525 | 0% | 6 | 525 | 72.1 | 452.9 | very similar observations as exp 4. CXP3058 gives a better particle size than 8181 but water clarity doesn't finish as well. Less pin floc with 2537A vs 1580.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 124 | 76.38% | 5
|  |  | 3 | 8181 | 1 | 2537A | 20 | 20 ppm:2537A 1 ppm:8181 | 105 | 80% | 4
|  |  | 4 | 8181 | 1 | 2537A | 25 | 25 ppm:2537A 1 ppm:8181 | 95.5 | 81.81% | 2
|  |  | 5 | 8181 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:8181 | 72.1 | 86.27% | 1
|  |  | 6 | 3058 | 1 | 2537A | 30 | 30 ppm:2537A 1 ppm:3058 | 104 | 80.19% | 3
2022-07-20 | 6 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 545 | 0% | 6 | 545 | 60.5 | 484.5 | addition of 18114 did give a cloudier mixture than previous coags and it increase with more coag. Particle size was biggest with cxp3058. settling rate J6>J2>j3>j4>j5
|  |  | 2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 174 | 68.07% | 5
|  |  | 3 | 8181 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:8181 | 92.2 | 83.08% | 4
|  |  | 4 | 8181 | 1 | 18114 | 25 | 25 ppm:18114 1 ppm:8181 | 81.2 | 85.1% | 3
|  |  | 5 | 8181 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:8181 | 70.6 | 87.05% | 2
|  |  | 6 | 3058 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:3058 | 60.5 | 88.9% | 1
2022-07-20 | 7 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 472 | 0% | 6 | 472 | 60.1 | 411.9 | there is an increase in FW as dosage increase. Not much of a noticeable change in floc size. J6>j5>j4>j3>j2>j1 for settling rates
|  |  | 2 | 8181 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:8181 | 248 | 47.46% | 5
|  |  | 3 | 8181 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:8181 | 158 | 66.53% | 4
|  |  | 4 | 8181 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:8181 | 119 | 74.79% | 3
|  |  | 5 | 8181 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:8181 | 63 | 86.65% | 2
|  |  | 6 | 8181 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:8181 | 60.1 | 87.27% | 1
2022-07-20 | 8 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 393 | 0% | 5 | 520 | 90.3 | 429.7 | same obs as exp 7
|  |  | 2 | 8181 | 0.5 | 1580 | 10 | 10 ppm:1580 0.5 ppm:8181 | 520 | -32.32% | 6
|  |  | 3 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 240 | 38.93% | 4
|  |  | 4 | 8181 | 1.5 | 1580 | 10 | 10 ppm:1580 1.5 ppm:8181 | 141 | 64.12% | 3
|  |  | 5 | 8181 | 2 | 1580 | 10 | 10 ppm:1580 2 ppm:8181 | 103 | 73.79% | 2
|  |  | 6 | 8181 | 2.5 | 1580 | 10 | 10 ppm:1580 2.5 ppm:8181 | 90.3 | 77.02% | 1
2022-07-20 | 9 | slurry method | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 999 | 0% | 6 | 999 | 168 | 831 | same obs as exp 7, no big effect with coag but doasge is low.
|  |  | 2 | 8181 | 0.5 | 18114 | 10 | 10 ppm:18114 0.5 ppm:8181 | 873 | 12.61% | 5
|  |  | 3 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 539 | 46.05% | 4
|  |  | 4 | 8181 | 1.5 | 18114 | 10 | 10 ppm:18114 1.5 ppm:8181 | 346 | 65.37% | 3
|  |  | 5 | 8181 | 2 | 18114 | 10 | 10 ppm:18114 2 ppm:8181 | 340 | 65.97% | 2
|  |  | 6 | 8181 | 2.5 | 18114 | 10 | 10 ppm:18114 2.5 ppm:8181 | 168 | 83.18% | 1
2022-07-21 | 10 | slurry method | 1 | 8181 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:8181 | 141 | 0% | 6 | 141 | 31.1 | 109.9 | J3 looks the best with large particles and lots of FW even during both stir periods. Particle size largest J5<J1<J6<J2<J4<J3. settling rate 16>15>24>25>31>38 for j4>j3>j1>j2>j5>j6. j6 finished the best with water clarity
|  |  | 2 | 7878 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7878 | 57.5 | 59.22% | 2
|  |  | 3 | 7767 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:7767 | 82.9 | 41.21% | 4
|  |  | 4 | 3058 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3058 | 134 | 4.965% | 5
|  |  | 5 | 3090 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:3090 | 73.6 | 47.8% | 3
|  |  | 6 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 31.1 | 77.94% | 1
2022-07-21 | 11 | slurry method | 1 | 8181 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:8181 | 115 | 0% | 3 | 277 | 43.1 | 233.9 | very similar trend with particle size as exp 10. J3 lots of FW. J4 15, J3 16, j1 24, j6 27, then j2 and J5. water clarity looks best in J6.
|  |  | 2 | 7878 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7878 | 166 | -44.35% | 4
|  |  | 3 | 7767 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:7767 | 183 | -59.13% | 5
|  |  | 4 | 3058 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:3058 | 277 | -140.9% | 6
|  |  | 5 | 3090 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:3090 | 106 | 7.826% | 2
|  |  | 6 | 61610 | 1 | 1580 | 10 | 10 ppm:1580 1 ppm:61610 | 43.1 | 62.52% | 1
2022-07-21 | 12 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 404 | 0% | 6 | 404 | 99.9 | 304.1 | very good dosage response, with large particle size and lots of FW. Settling rate is j6>j5>j4>j3>j2>j1
|  |  | 2 | 3058 | 0.5 | 2537A | 10 | 10 ppm:2537A 0.5 ppm:3058 | 327 | 19.06% | 5
|  |  | 3 | 3058 | 1 | 2537A | 10 | 10 ppm:2537A 1 ppm:3058 | 302 | 25.25% | 4
|  |  | 4 | 3058 | 1.5 | 2537A | 10 | 10 ppm:2537A 1.5 ppm:3058 | 204 | 49.5% | 3
|  |  | 5 | 3058 | 2 | 2537A | 10 | 10 ppm:2537A 2 ppm:3058 | 137 | 66.09% | 2
|  |  | 6 | 3058 | 2.5 | 2537A | 10 | 10 ppm:2537A 2.5 ppm:3058 | 99.9 | 75.27% | 1
2022-07-21 | 13 | slurry | 1 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 39 | 0% | 3 | 121 | 31.9 | 89.1 | good particle growth with increased floc. Settling rate increased likewise and all faster than settling rates for J4-6. no difference between J4-J6. collected at 3 min mark.
|  |  | 2 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 52.9 | -35.64% | 4
|  |  | 3 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 121 | -210.3% | 6
|  |  | 4 | 61610 | 1 | 18114 | 10 | 10 ppm:18114 1 ppm:61610 | 65.8 | -68.72% | 5
|  |  | 5 | 61610 | 1 | 18114 | 20 | 20 ppm:18114 1 ppm:61610 | 34.8 | 10.77% | 2
|  |  | 6 | 61610 | 1 | 18114 | 30 | 30 ppm:18114 1 ppm:61610 | 31.9 | 18.21% | 1
2022-08-03 | 14 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 322 | 0% | 6 | 322 | 43.1 | 278.9 | J3 & J5 has the most FW during stir, particle size looks smallest in J6. settling rates for J2-J5 very similar, J6 is the slowest. Collect at 3 min.
|  |  | 2 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 108 | 66.46% | 5
|  |  | 3 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 96 | 70.19% | 4
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 91.4 | 71.61% | 3
|  |  | 5 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 43.1 | 86.61% | 1
|  |  | 6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 60.4 | 81.24% | 2
2022-08-03 | 15 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 371 | 0% | 6 | 371 | 77.3 | 293.7 | 18114 gives cloudiness and it increases with dosgae increase. More floc larger particles & faster settling. The settling rate does seem to slow with more coag. Much better water clarity with increased coag. Sludge bed is less compact with high coag, 150 mL at 30 ppm, 125 at 20 and 120 at 15.
|  |  | 2 | 8181 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:8181 | 104 | 71.97% | 3
|  |  | 3 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 116 | 68.73% | 4
|  |  | 4 | 8181 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:8181 | 129 | 65.23% | 5
|  |  | 5 | 8181 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:8181 | 100 | 73.05% | 2
|  |  | 6 | 8181 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:8181 | 77.3 | 79.16% | 1
2022-08-03 | 16 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 552 | 0% | 6 | 552 | 40.7 | 511.3 | same cloudiness. But no diff in particle size. J2 fastest settling, followed by J3. no diff in settling between J4-J6. no difference in sludge compaction
|  |  | 2 | 61610 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:61610 | 60.7 | 89% | 3
|  |  | 3 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 65.5 | 88.13% | 4
|  |  | 4 | 61610 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:61610 | 95 | 82.79% | 5
|  |  | 5 | 61610 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:61610 | 43.4 | 92.14% | 2
|  |  | 6 | 61610 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:61610 | 40.7 | 92.63% | 1
2022-08-03 | 17 | slurry | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 346 | 0% | 6 | 346 | 37.6 | 308.4 | excellent response with Lrger particle as floc increases, coag doesn't affect size. Lots of FW in all jars. Much faster settling rate with 7878 over other flocs. J2>J3>J4>J5>J6…more coags slows settling slightly.
|  |  | 2 | 7878 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:7878 | 37.6 | 89.13% | 1
|  |  | 3 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 52.8 | 84.74% | 3
|  |  | 4 | 7878 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:7878 | 88 | 74.57% | 5
|  |  | 5 | 7878 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:7878 | 64.8 | 81.27% | 4
|  |  | 6 | 7878 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:7878 | 45 | 86.99% | 2
2022-08-03 | 18 | settling test - use slurry procedure with 20% sludge | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 533 | 0% | 6 | 533 | 151 | 382 | no particle size growth difference bt the jars. J4-6 had the same particel size. There is a slight increase in settling rate with more floc. 5 min settling
|  |  | 2 | 8181 | 0.5 | 2537A | 30 | 30 ppm:2537A 0.5 ppm:8181 | 151 | 71.67% | 1
|  |  | 3 | 8181 | 0.5 | 2537A | 20 | 20 ppm:2537A 0.5 ppm:8181 | 172 | 67.73% | 2
|  |  | 4 | 8181 | 0.5 | 2537A | 15 | 15 ppm:2537A 0.5 ppm:8181 | 425 | 20.26% | 5
|  |  | 5 | 8181 | 1 | 2537A | 15 | 15 ppm:2537A 1 ppm:8181 | 318 | 40.34% | 3
|  |  | 6 | 8181 | 1.5 | 2537A | 15 | 15 ppm:2537A 1.5 ppm:8181 | 332 | 37.71% | 4
2022-08-03 | 19 | settling test - use slurry procedure with 20% sludge | 1 | 8181 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:8181 | 541 | 0% | 6 | 541 | 132 | 409 | 18114 jars all showed a particulate formation but not 1580. j4 looked the best during the stir period. 7878 jars showed the fastest settling
|  |  | 2 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 | 522 | 3.512% | 5
|  |  | 3 | 7878 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:7878 | 305 | 43.62% | 4
|  |  | 4 | 7878 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:7878 | 147 | 72.83% | 2
|  |  | 5 | 61610 | 1 | 1580 | 15 | 15 ppm:1580 1 ppm:61610 | 216 | 60.07% | 3
|  |  | 6 | 61610 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:61610 | 132 | 75.6% | 1
2022-08-03 | 20 | settling test - use slurry procedure with 20% sludge | 1 | 8181 | 0.5 | 18114 | 30 | 30 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A | 0 | 0 | 0
|  |  | 2 | 8181 | 0.5 | 18114 | 20 | 20 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 3 | 8181 | 0.5 | 18114 | 15 | 15 ppm:18114 0.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 4 | 8181 | 1 | 18114 | 15 | 15 ppm:18114 1 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 5 | 8181 | 1.5 | 18114 | 15 | 15 ppm:18114 1.5 ppm:8181 |  | #DIV/0! | #N/A
|  |  | 6 | 8181 | 1.5 | 18114 | 30 | 30 ppm:18114 1.5 ppm:8181 |  | #DIV/0! | #N/A

## 2021 Summer
Date | Procedure | Test | Jar | Floc | Dosage (ppm) | Coag | Dosage (ppm) | Coagulant:Flocculant | Turbs | RANK | MAX | MIN | RANGE | Comment
2021-08-17 | Composite | 1 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 107 | 6 | 107 | 9.39 | 97.61 | there is a particle size incease with 2495 vs all of the other jars. Also settles fastest with best water clarity
|  |  | 2 | blank | 0 | 1252 | 10 | 10 ppm:1252 0 ppm:blank | 76 | 4
|  |  | 3 | blank | 0 | 2537 | 10 | 10 ppm:2537 0 ppm:blank | 67.5 | 2
|  |  | 4 | blank | 0 | 2495 | 10 | 10 ppm:2495 0 ppm:blank | 9.39 | 1
|  |  | 5 | blank | 0 | 17650 | 10 | 10 ppm:17650 0 ppm:blank | 71.5 | 3
|  |  | 6 | blank | 0 | 8190 | 10 | 10 ppm:8190 0 ppm:blank | 96.6 | 5
2021-08-17 |  | 2 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 133 | 6 | 133 | 11.7 | 121.3 | particle size increase with floc increase, fw during stir period in j5&6. very similar behaviour from Oct testing. This is a good product combo in terms of water quality
|  |  | 2 | 2531 | 0.2 | 1252 | 10 | 10 ppm:1252 0.2 ppm:2531 | 79 | 5
|  |  | 3 | 2531 | 0.4 | 1252 | 10 | 10 ppm:1252 0.4 ppm:2531 | 51.8 | 4
|  |  | 4 | 2531 | 0.6 | 1252 | 10 | 10 ppm:1252 0.6 ppm:2531 | 29.9 | 3
|  |  | 5 | 2531 | 0.8 | 1252 | 10 | 10 ppm:1252 0.8 ppm:2531 | 21.8 | 2
|  |  | 6 | 2531 | 1 | 1252 | 10 | 10 ppm:1252 1 ppm:2531 | 11.7 | 1
2021-08-18 |  | 3 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 91 | 6 | 91 | 6.22 | 84.78
|  |  | 2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 43.2 | 3
|  |  | 3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 27.1 | 2
|  |  | 4 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 6.22 | 1
|  |  | 5 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 54 | 4
|  |  | 6 | 7878 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7878 | 59.6 | 5
2021-08-18 |  | 4 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 98.9 | 6 | 98.9 | 4.78 | 94.12 | 7767 shows much better floc formation than 7878 in al jars. Can see FW in both fast and slow stir. 17650 appears to settle fastest but water quality is not as good as 2537 or 2495.
|  |  | 2 | 2531 | 0.5 | 1252 | 10 | 10 ppm:1252 0.5 ppm:2531 | 25.7 | 3
|  |  | 3 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 7.92 | 2
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.78 | 1
|  |  | 5 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.2 | 4
|  |  | 6 | 7767 | 0.5 | 8190 | 10 | 10 ppm:8190 0.5 ppm:7767 | 34.8 | 5
2021-08-18 |  | 5 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 91.5 | 6 | 91.5 | 10.4 | 81.1 | J4 & J6 shows large particle size and lots of FW during stirring. J6>J4>JJ2>J1>J5>J3 in terms of settling rate. J6 is showing best water quality
|  |  | 2 | 2531 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:2531 | 14.2 | 2
|  |  | 3 | 7878 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7878 | 55.2 | 4
|  |  | 4 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 32.6 | 3
|  |  | 5 | 7757 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7757 | 57.3 | 5
|  |  | 6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 10.4 | 1
2021-08-18 |  | 6 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 89.3 | 6 | 89.3 | 3.65 | 85.65 | similar trend as exp 5 with J6 & J4 showing best response. All excellent results wwith 2495, this is same as previous jar testing where 2495 made everything look great. However, 8181 does rank the best.
|  |  | 2 | 2531 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:2531 | 4.2 | 2
|  |  | 3 | 7878 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7878 | 5.39 | 5
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 4.67 | 3
|  |  | 5 | 7757 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7757 | 4.93 | 4
|  |  | 6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 3.65 | 1
2021-08-18 |  | 7 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 66.2 | 6 | 66.2 | 6.4 | 59.8 | same trend as above. Really liking the response with 8181. J6 & J4 fastesst settling. J 3 & J5 are the slowest, this is interesting since the blank actually settles faster than jars with 7878 or 7757 present.
|  |  | 2 | 2531 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:2531 | 11.4 | 3
|  |  | 3 | 7878 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7878 | 25.4 | 5
|  |  | 4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 6.4 | 1
|  |  | 5 | 7757 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7757 | 19 | 4
|  |  | 6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 8.28 | 2
2021-08-18 |  | 8 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 52.4 | 6 | 52.4 | 15.2 | 37.2 | these jars all look good.
|  |  | 2 | 7767 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:7767 | 36 | 5
|  |  | 3 | 7767 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:7767 | 24.5 | 4
|  |  | 4 | 7767 | 0.5 | 17650 | 15 | 15 ppm:17650 0.5 ppm:7767 | 21.8 | 3
|  |  | 5 | 8181 | 0.5 | 17650 | 5 | 5 ppm:17650 0.5 ppm:8181 | 16.6 | 2
|  |  | 6 | 8181 | 0.5 | 17650 | 10 | 10 ppm:17650 0.5 ppm:8181 | 15.2 | 1
2021-08-18 |  | 9 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 94.9 | 6 | 94.9 | 4.36 | 90.54 | all fast settling, excellent water quality. Collected at 2 min mark
|  |  | 2 | 7767 | 0.5 | 2495 | 2.5 | 2.5 ppm:2495 0.5 ppm:7767 | 20.2 | 5
|  |  | 3 | 7767 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:7767 | 10.7 | 4
|  |  | 4 | 7767 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:7767 | 5.48 | 2
|  |  | 5 | 8181 | 0.5 | 2495 | 5 | 5 ppm:2495 0.5 ppm:8181 | 9.03 | 3
|  |  | 6 | 8181 | 0.5 | 2495 | 10 | 10 ppm:2495 0.5 ppm:8181 | 4.36 | 1
2021-08-19 |  | 10 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 162 | 6 | 162 | 4.99 | 157.01 | same trends as above. 8181 does an excellent job at particle size. Colleccted turbs at 2 min settling.
|  |  | 2 | 7767 | 0.5 | 2537 | 2.5 | 2.5 ppm:2537 0.5 ppm:7767 | 21 | 5
|  |  | 3 | 7767 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:7767 | 11.6 | 2
|  |  | 4 | 7767 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:7767 | 4.99 | 1
|  |  | 5 | 8181 | 0.5 | 2537 | 5 | 5 ppm:2537 0.5 ppm:8181 | 18.7 | 4
|  |  | 6 | 8181 | 0.5 | 2537 | 10 | 10 ppm:2537 0.5 ppm:8181 | 12.4 | 3
2021-08-19 |  | 11 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 264 | 6 | 264 | 10.7 | 253.3 | excellent dosage profile, nice gradient with increased particle size, settling rate & clarity. Collected turb @ 2mins
|  |  | 2 | 7767 | 0.2 | 2537 | 5 | 5 ppm:2537 0.2 ppm:7767 | 25.8 | 5
|  |  | 3 | 7767 | 0.4 | 2537 | 5 | 5 ppm:2537 0.4 ppm:7767 | 19.6 | 4
|  |  | 4 | 7767 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:7767 | 13.4 | 3
|  |  | 5 | 7767 | 0.8 | 2537 | 5 | 5 ppm:2537 0.8 ppm:7767 | 11.4 | 2
|  |  | 6 | 7767 | 1 | 2537 | 5 | 5 ppm:2537 1 ppm:7767 | 10.7 | 1
2021-08-19 |  | 12 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 105 | 6 | 105 | 7.76 | 97.24 | excellent dosage profile
|  |  | 2 | 7767 | 0.2 | 2495 | 5 | 5 ppm:2495 0.2 ppm:7767 | 25 | 5
|  |  | 3 | 7767 | 0.4 | 2495 | 5 | 5 ppm:2495 0.4 ppm:7767 | 14.2 | 4
|  |  | 4 | 7767 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:7767 | 9.46 | 3
|  |  | 5 | 7767 | 0.8 | 2495 | 5 | 5 ppm:2495 0.8 ppm:7767 | 7.76 | 1
|  |  | 6 | 7767 | 1 | 2495 | 5 | 5 ppm:2495 1 ppm:7767 | 8.7 | 2
2021-08-19 |  | 13 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 161 | 6 | 161 | 23.4 | 137.6 | lots of FW with increasing floc, large particle size. Settling rate very fast with increasing floc. The sludge is so thick the settling rates are likely skewed as a result. 2min turb
|  |  | 2 | 7767 | 0.2 | 17650 | 10 | 10 ppm:17650 0.2 ppm:7767 | 48.9 | 5
|  |  | 3 | 7767 | 0.4 | 17650 | 10 | 10 ppm:17650 0.4 ppm:7767 | 32.5 | 4
|  |  | 4 | 7767 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:7767 | 26.4 | 3
|  |  | 5 | 7767 | 0.8 | 17650 | 10 | 10 ppm:17650 0.8 ppm:7767 | 25.1 | 2
|  |  | 6 | 7767 | 1 | 17650 | 10 | 10 ppm:17650 1 ppm:7767 | 23.4 | 1
2021-08-19 |  | 14 | 1 | 8181 | 0.3 | 17650 | 10 | 10 ppm:17650 0.3 ppm:8181 | 58.6 | 6 | 58.6 | 8.27 | 50.33 | marked difference with 2495 vs 2537 & 17650…FW is observed just with coag addition. Then with floc the particle size is definitely larger for 2495. settling rates are all very fast2 min turbs
|  |  | 2 | 8181 | 0.6 | 17650 | 10 | 10 ppm:17650 0.6 ppm:8181 | 22 | 4
|  |  | 3 | 8181 | 0.3 | 2495 | 5 | 5 ppm:2495 0.3 ppm:8181 | 17.2 | 3
|  |  | 4 | 8181 | 0.6 | 2495 | 5 | 5 ppm:2495 0.6 ppm:8181 | 8.27 | 1
|  |  | 5 | 8181 | 0.3 | 2537 | 5 | 5 ppm:2537 0.3 ppm:8181 | 34.8 | 5
|  |  | 6 | 8181 | 0.6 | 2537 | 5 | 5 ppm:2537 0.6 ppm:8181 | 9.03 | 2
2021-08-19 |  | 15 | 1 | blank | 0 | blank | 0 | 0 ppm:blank 0 ppm:blank | 218 | 6 | 218 | 10.8 | 207.2 | this was supposed to be exp 12 but screwed up the coag addition so just went with it and removed the floc. This does show the impact of just coag 2495 with nice gradient in performance. Collected at 2min
|  |  | 2 | blank | 0 | 2495 | 2 | 2 ppm:2495 0 ppm:blank | 70.2 | 5
|  |  | 3 | blank | 0 | 2495 | 4 | 4 ppm:2495 0 ppm:blank | 43.9 | 4
|  |  | 4 | blank | 0 | 2495 | 6 | 6 ppm:2495 0 ppm:blank | 28.4 | 3
|  |  | 5 | blank | 0 | 2495 | 8 | 8 ppm:2495 0 ppm:blank | 14.9 | 2
|  |  | 6 | blank | 0 | 2495 | 10 | 10 ppm:2495 0 ppm:blank | 10.8 | 1